## FMS Heating
AQUILO FMS -Heating only | [24 empty] | 070721 MII
Re corrected heat outputs
Re corrected flow resistances
ΔT according to DIN 4703-3: | [6 empty] | Tflow = | 75 | oC
[7 empty] | Trtn = | 65 | oC
[7 empty] | Tin = | 20 | oC
[7 empty] | ΔTar = | 50 | K
Standard heat outputs at dT50K
FMS 90 | [6 empty] | FMS 110 | [6 empty] | FMS 140 | [5 empty] | FMS 190
Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  | Length |  |  | Width B, mm
Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 | Lc, mm | 200 | 250 | 300 | 340 | 420
700 | 110 | 137 | 176 | 194 | 228 |  | 700 | 121 | 161 | 213 | 232 | 278 |  | 700 | 134 | 199 | 238 | 276 | 325 | 700 | 138 | 226 | 300 | 364 | 449
800 | 134 | 166 | 215 | 237 | 277 |  | 800 | 148 | 196 | 260 | 282 | 338 |  | 800 | 163 | 242 | 290 | 337 | 395 | 800 | 169 | 275 | 365 | 444 | 547
900 | 158 | 196 | 253 | 279 | 327 |  | 900 | 174 | 231 | 306 | 332 | 399 |  | 900 | 193 | 285 | 341 | 397 | 466 | 900 | 199 | 325 | 430 | 523 | 645
1000 | 182 | 226 | 291 | 321 | 377 |  | 1000 | 200 | 266 | 353 | 383 | 459 |  | 1000 | 222 | 328 | 393 | 457 | 537 | 1000 | 229 | 374 | 496 | 602 | 742
1100 | 206 | 255 | 330 | 363 | 426 |  | 1100 | 227 | 301 | 399 | 433 | 520 |  | 1100 | 251 | 371 | 445 | 517 | 607 | 1100 | 259 | 423 | 561 | 681 | 840
1200 | 230 | 285 | 368 | 406 | 476 |  | 1200 | 253 | 336 | 445 | 483 | 580 |  | 1200 | 280 | 414 | 496 | 577 | 678 | 1200 | 289 | 472 | 626 | 761 | 937
1300 | 254 | 315 | 406 | 448 | 525 |  | 1300 | 280 | 372 | 492 | 534 | 640 |  | 1300 | 309 | 458 | 548 | 637 | 748 | 1300 | 319 | 521 | 691 | 840 | 1035
1400 | 278 | 344 | 445 | 490 | 575 |  | 1400 | 306 | 407 | 538 | 584 | 701 |  | 1400 | 339 | 501 | 600 | 697 | 819 | 1400 | 349 | 571 | 756 | 919 | 1133
1500 | 302 | 374 | 483 | 532 | 624 |  | 1500 | 332 | 442 | 584 | 635 | 761 |  | 1500 | 368 | 544 | 652 | 757 | 890 | 1500 | 379 | 620 | 822 | 998 | 1230
1600 | 326 | 404 | 521 | 575 | 674 |  | 1600 | 359 | 477 | 631 | 685 | 822 |  | 1600 | 397 | 587 | 703 | 817 | 960 | 1600 | 409 | 669 | 887 | 1078 | 1328
1800 | 374 | 463 | 598 | 659 | 773 |  | 1800 | 411 | 547 | 724 | 786 | 942 |  | 1800 | 455 | 673 | 807 | 938 | 1102 | 1800 | 470 | 767 | 1017 | 1236 | 1523
2000 | 422 | 523 | 675 | 744 | 872 |  | 2000 | 464 | 617 | 816 | 886 | 1063 |  | 2000 | 514 | 760 | 910 | 1058 | 1243 | 2000 | 530 | 866 | 1148 | 1395 | 1719
2200 | 470 | 582 | 751 | 828 | 971 |  | 2200 | 517 | 687 | 909 | 987 | 1184 |  | 2200 | 572 | 846 | 1014 | 1178 | 1384 | 2200 | 590 | 964 | 1278 | 1553 | 1914
2400 | 518 | 641 | 828 | 912 | 1070 |  | 2400 | 570 | 757 | 1002 | 1088 | 1305 |  | 2400 | 630 | 932 | 1117 | 1298 | 1525 | 2400 | 650 | 1062 | 1408 | 1711 | 2109
2500 | 542 | 671 | 866 | 955 | 1120 |  | 2500 | 596 | 792 | 1048 | 1138 | 1365 |  | 2500 | 660 | 975 | 1169 | 1358 | 1596 | 2500 | 680 | 1112 | 1474 | 1791 | 2207
2600 | 566 | 701 | 905 | 997 | 1169 |  | 2600 | 623 | 827 | 1095 | 1188 | 1426 |  | 2600 | 689 | 1019 | 1220 | 1418 | 1666 | 2600 | 710 | 1161 | 1539 | 1870 | 2305
2700 | 590 | 730 | 943 | 1039 | 1219 |  | 2700 | 649 | 862 | 1141 | 1239 | 1486 |  | 2700 | 718 | 1062 | 1272 | 1479 | 1737 | 2700 | 741 | 1210 | 1604 | 1949 | 2402
2800 | 614 | 760 | 981 | 1081 | 1268 |  | 2800 | 675 | 897 | 1187 | 1289 | 1546 |  | 2800 | 747 | 1105 | 1324 | 1539 | 1808 | 2800 | 771 | 1259 | 1669 | 2028 | 2500
2900 | 638 | 790 | 1019 | 1124 | 1318 |  | 2900 | 702 | 932 | 1234 | 1340 | 1607 |  | 2900 | 776 | 1148 | 1376 | 1599 | 1878 | 2900 | 801 | 1308 | 1734 | 2108 | 2598
3000 | 662 | 820 | 1058 | 1166 | 1367 |  | 3000 | 728 | 967 | 1280 | 1390 | 1667 |  | 3000 | 805 | 1191 | 1427 | 1659 | 1949 | 3000 | 831 | 1357 | 1800 | 2187 | 2695
3200 | 710 | 879 | 1134 | 1250 | 1466 |  | 3200 | 781 | 1038 | 1373 | 1491 | 1788 |  | 3200 | 864 | 1278 | 1531 | 1779 | 2090 | 3200 | 891 | 1456 | 1930 | 2345 | 2891
3400 | 758 | 938 | 1211 | 1335 | 1565 |  | 3400 | 834 | 1108 | 1466 | 1591 | 1909 |  | 3400 | 922 | 1364 | 1634 | 1899 | 2231 | 3400 | 951 | 1554 | 2060 | 2504 | 3086
3600 | 806 | 998 | 1288 | 1419 | 1665 |  | 3600 | 886 | 1178 | 1558 | 1692 | 2030 |  | 3600 | 981 | 1450 | 1738 | 2019 | 2373 | 3600 | 1011 | 1653 | 2191 | 2662 | 3281
Reynolds number |  |  | Example |  | Inner diameter of the pipe |  |  | 15.1 | mm |  |  | Surface roughness | 0.024 | mm
[5 empty] | Water flow rate |  |  | 69 | l/h |  |  | Real inner diameter | 15.1 | mm
[5 empty] | Mean water temperature |  |  | 70 | °C
[5 empty] | Water flow speed |  |  | 0.10702 | m/s
[7 empty] | r | 977.712 | kg/m3
[7 empty] | n | 0.42467 | 10-6 m2/s
[6 empty] | Reynolds number | Re | 3805.1472
Reynolds numbers at standard output conditions 75/65/20
FMS 90 | [6 empty] | FMS 110 | [6 empty] | FMS 140 | [5 empty] | FMS 190
Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  | Length |  |  | Width B, mm
Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 | Lc, mm | 200 | 250 | 300 | 340 | 420
700 | 514.053 | 640.2297 | 822.4848 | 906.6026 | 1065.4917 |  | 700 | 565.4583 | 752.3867 | 995.3936 | 1084.1845 | 1299.1522 |  | 700 | 626.21 | 929.9686 | 1112.2238 | 1289.8057 | 1518.793 | 700 | 644.9029 | 1056.1453 | 1401.9628 | 1701.0481 | 2098.2709
800 | 626.21 | 775.7527 | 1004.74 | 1107.5506 | 1294.4789 |  | 800 | 691.635 | 915.949 | 1215.0344 | 1317.845 | 1579.5447 |  | 800 | 761.7331 | 1130.9166 | 1355.2307 | 1574.8715 | 1845.9176 | 800 | 789.7724 | 1285.1325 | 1705.7214 | 2074.9049 | 2556.2454
900 | 738.3671 | 915.949 | 1182.3219 | 1303.8254 | 1528.1394 |  | 900 | 813.1384 | 1079.5113 | 1430.002 | 1551.5055 | 1864.6105 |  | 900 | 901.9294 | 1331.8646 | 1593.5643 | 1855.2641 | 2177.7155 | 900 | 929.9686 | 1518.793 | 2009.48 | 2444.0884 | 3014.2199
1000 | 850.5241 | 1056.1453 | 1359.9039 | 1500.1002 | 1761.7999 |  | 1000 | 934.6418 | 1243.0736 | 1649.6428 | 1789.8391 | 2145.003 |  | 1000 | 1037.4524 | 1532.8126 | 1836.5712 | 2135.6566 | 2509.5133 | 1000 | 1070.1649 | 1747.7802 | 2317.9118 | 2813.2719 | 3467.5212
1100 | 962.6811 | 1191.6683 | 1542.159 | 1696.3749 | 1990.7871 |  | 1100 | 1060.8185 | 1406.636 | 1864.6105 | 2023.4996 | 2430.0688 |  | 1100 | 1172.9755 | 1733.7606 | 2079.5781 | 2416.0492 | 2836.638 | 1100 | 1210.3612 | 1976.7675 | 2621.6704 | 3182.4555 | 3925.4957
1200 | 1074.8381 | 1331.8646 | 1719.741 | 1897.3229 | 2224.4476 |  | 1200 | 1182.3219 | 1570.1983 | 2079.5781 | 2257.16 | 2710.4613 |  | 1200 | 1308.4986 | 1934.7086 | 2317.9118 | 2696.4417 | 3168.4358 | 1200 | 1350.5575 | 2205.7547 | 2925.429 | 3556.3122 | 4378.797
1300 | 1186.9951 | 1472.0609 | 1897.3229 | 2093.5977 | 2453.4348 |  | 1300 | 1308.4986 | 1738.4338 | 2299.2189 | 2495.4937 | 2990.8539 |  | 1300 | 1444.0216 | 2140.3298 | 2560.9186 | 2976.8343 | 3495.5605 | 1300 | 1490.7537 | 2434.742 | 3229.1876 | 3925.4957 | 4836.7715
1400 | 1299.1522 | 1607.584 | 2079.5781 | 2289.8725 | 2687.0953 |  | 1400 | 1430.002 | 1901.9961 | 2514.1866 | 2729.1542 | 3275.9197 |  | 1400 | 1584.2179 | 2341.2778 | 2803.9255 | 3257.2268 | 3827.3583 | 1400 | 1630.95 | 2668.4025 | 3532.9462 | 4294.6793 | 5294.746
1500 | 1411.3092 | 1747.7802 | 2257.16 | 2486.1473 | 2916.0825 |  | 1500 | 1551.5055 | 2065.5585 | 2729.1542 | 2967.4878 | 3556.3122 |  | 1500 | 1719.741 | 2542.2258 | 3046.9324 | 3537.6194 | 4159.1562 | 1500 | 1771.1463 | 2897.3897 | 3841.378 | 4663.8628 | 5748.0473
1600 | 1523.4662 | 1887.9765 | 2434.742 | 2687.0953 | 3149.743 |  | 1600 | 1677.6821 | 2229.1208 | 2948.795 | 3201.1483 | 3841.378 |  | 1600 | 1855.2641 | 2743.1738 | 3285.2661 | 3818.0119 | 4486.2808 | 1600 | 1911.3426 | 3126.377 | 4145.1366 | 5037.7195 | 6206.0218
1800 | 1747.7802 | 2163.6959 | 2794.5791 | 3079.6449 | 3612.3907 |  | 1800 | 1920.689 | 2556.2454 | 3383.4035 | 3673.1424 | 4402.1631 |  | 1800 | 2126.3102 | 3145.0698 | 3771.2798 | 4383.4702 | 5149.8765 | 1800 | 2196.4083 | 3584.3515 | 4752.6538 | 5776.0866 | 7117.2976
2000 | 1972.0943 | 2444.0884 | 3154.4162 | 3476.8676 | 4075.0384 |  | 2000 | 2168.3691 | 2883.3701 | 3813.3387 | 4140.4634 | 4967.6214 |  | 2000 | 2402.0295 | 3551.639 | 4252.6204 | 4944.2553 | 5808.799 | 2000 | 2476.8009 | 4046.9992 | 5364.8442 | 6519.1268 | 8033.2466
2200 | 2196.4083 | 2719.8078 | 3509.5801 | 3869.4172 | 4537.6861 |  | 2200 | 2416.0492 | 3210.4947 | 4247.9472 | 4612.4575 | 5533.0797 |  | 2200 | 2673.0757 | 3953.535 | 4738.6341 | 5505.0404 | 6467.7215 | 2200 | 2757.1934 | 4504.9737 | 5972.3614 | 7257.4939 | 8944.5224
2400 | 2420.7224 | 2995.5271 | 3869.4172 | 4261.9668 | 5000.3338 |  | 2400 | 2663.7292 | 3537.6194 | 4682.5556 | 5084.4516 | 6098.538 |  | 2400 | 2944.1218 | 4355.431 | 5219.9747 | 6065.8255 | 7126.644 | 2400 | 3037.586 | 4962.9482 | 6579.8786 | 7995.8609 | 9855.7982
2500 | 2532.8794 | 3135.7234 | 4046.9992 | 4462.9148 | 5233.9943 |  | 2500 | 2785.2327 | 3701.1817 | 4897.5232 | 5318.1121 | 6378.9306 |  | 2500 | 3084.3181 | 4556.379 | 5462.9816 | 6346.2181 | 7458.4419 | 2500 | 3177.7823 | 5196.6086 | 6888.3104 | 8369.7177 | 10313.7727
2600 | 2645.0364 | 3275.9197 | 4229.2543 | 4659.1896 | 5462.9816 |  | 2600 | 2911.4093 | 3864.744 | 5117.1641 | 5551.7725 | 6663.9963 |  | 2600 | 3219.8411 | 4762.0002 | 5701.3152 | 6626.6106 | 7785.5665 | 2600 | 3317.9785 | 5425.5959 | 7192.069 | 8738.9012 | 10771.7472
2700 | 2757.1934 | 3411.4427 | 4406.8363 | 4855.4644 | 5696.642 |  | 2700 | 3032.9128 | 4028.3063 | 5332.1317 | 5790.1062 | 6944.3889 |  | 2700 | 3355.3642 | 4962.9482 | 5944.3221 | 6911.6764 | 8117.3644 | 2700 | 3462.848 | 5654.5831 | 7495.8276 | 9108.0847 | 11225.0485
2800 | 2869.3504 | 3551.639 | 4584.4182 | 5051.7391 | 5925.6293 |  | 2800 | 3154.4162 | 4191.8687 | 5547.0993 | 6023.7667 | 7224.7814 |  | 2800 | 3490.8873 | 5163.8962 | 6187.329 | 7192.069 | 8449.1622 | 2800 | 3603.0443 | 5883.5704 | 7799.5862 | 9477.2683 | 11683.023
2900 | 2981.5075 | 3691.8353 | 4762.0002 | 5252.6871 | 6159.2897 |  | 2900 | 3280.5929 | 4355.431 | 5766.7402 | 6262.1003 | 7509.8472 |  | 2900 | 3626.4103 | 5364.8442 | 6430.3359 | 7472.4615 | 8776.2869 | 2900 | 3743.2406 | 6112.5576 | 8103.3448 | 9851.125 | 12140.9975
3000 | 3093.6645 | 3832.0315 | 4944.2553 | 5448.9619 | 6388.277 |  | 3000 | 3402.0963 | 4518.9933 | 5981.7078 | 6495.7608 | 7790.2397 |  | 3000 | 3761.9334 | 5565.7922 | 6668.6695 | 7752.8541 | 9108.0847 | 3000 | 3883.4368 | 6341.5449 | 8411.7766 | 10220.3085 | 12594.2988
3200 | 3317.9785 | 4107.7509 | 5299.4192 | 5841.5115 | 6850.9247 |  | 3200 | 3649.7764 | 4850.7912 | 6416.3162 | 6967.7549 | 8355.6981 |  | 3200 | 4037.6527 | 5972.3614 | 7154.6833 | 8313.6392 | 9767.0072 | 3200 | 4163.8294 | 6804.1926 | 9019.2938 | 10958.6756 | 13510.2478
3400 | 3542.2926 | 4383.4702 | 5659.2563 | 6238.7343 | 7313.5724 |  | 3400 | 3897.4565 | 5177.9158 | 6850.9247 | 7435.0758 | 8921.1564 |  | 3400 | 4308.6989 | 6374.2574 | 7636.0238 | 8874.4243 | 10425.9297 | 3400 | 4444.222 | 7262.1671 | 9626.811 | 11701.7158 | 14421.5236
3600 | 3766.6066 | 4663.8628 | 6019.0935 | 6631.2839 | 7780.8933 |  | 3600 | 4140.4634 | 5505.0404 | 7280.8599 | 7907.07 | 9486.6147 |  | 3600 | 4584.4182 | 6776.1533 | 8122.0376 | 9435.2094 | 11089.5254 | 3600 | 4724.6145 | 7724.8148 | 10239.0014 | 12440.0829 | 15332.7994
Heat outputs at calculation conditions without correction
FMS 90 | [6 empty] | FMS 110 | [6 empty] | FMS 140 | [5 empty] | FMS 190
Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  | Length |  |  | Width B, mm
Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 | Lc, mm | 200 | 250 | 300 | 340 | 420
700 | 110 | 137 | 176 | 194 | 228 |  | 700 | 121 | 161 | 213 | 232 | 278 |  | 700 | 134 | 199 | 238 | 276 | 325 | 700 | 138 | 226 | 300 | 364 | 449
800 | 134 | 166 | 215 | 237 | 277 |  | 800 | 148 | 196 | 260 | 282 | 338 |  | 800 | 163 | 242 | 290 | 337 | 395 | 800 | 169 | 275 | 365 | 444 | 547
900 | 158 | 196 | 253 | 279 | 327 |  | 900 | 174 | 231 | 306 | 332 | 399 |  | 900 | 193 | 285 | 341 | 397 | 466 | 900 | 199 | 325 | 430 | 523 | 645
1000 | 182 | 226 | 291 | 321 | 377 |  | 1000 | 200 | 266 | 353 | 383 | 459 |  | 1000 | 222 | 328 | 393 | 457 | 537 | 1000 | 229 | 374 | 496 | 602 | 742
1100 | 206 | 255 | 330 | 363 | 426 |  | 1100 | 227 | 301 | 399 | 433 | 520 |  | 1100 | 251 | 371 | 445 | 517 | 607 | 1100 | 259 | 423 | 561 | 681 | 840
1200 | 230 | 285 | 368 | 406 | 476 |  | 1200 | 253 | 336 | 445 | 483 | 580 |  | 1200 | 280 | 414 | 496 | 577 | 678 | 1200 | 289 | 472 | 626 | 761 | 937
1300 | 254 | 315 | 406 | 448 | 525 |  | 1300 | 280 | 372 | 492 | 534 | 640 |  | 1300 | 309 | 458 | 548 | 637 | 748 | 1300 | 319 | 521 | 691 | 840 | 1035
1400 | 278 | 344 | 445 | 490 | 575 |  | 1400 | 306 | 407 | 538 | 584 | 701 |  | 1400 | 339 | 501 | 600 | 697 | 819 | 1400 | 349 | 571 | 756 | 919 | 1133
1500 | 302 | 374 | 483 | 532 | 624 |  | 1500 | 332 | 442 | 584 | 635 | 761 |  | 1500 | 368 | 544 | 652 | 757 | 890 | 1500 | 379 | 620 | 822 | 998 | 1230
1600 | 326 | 404 | 521 | 575 | 674 |  | 1600 | 359 | 477 | 631 | 685 | 822 |  | 1600 | 397 | 587 | 703 | 817 | 960 | 1600 | 409 | 669 | 887 | 1078 | 1328
1800 | 374 | 463 | 598 | 659 | 773 |  | 1800 | 411 | 547 | 724 | 786 | 942 |  | 1800 | 455 | 673 | 807 | 938 | 1102 | 1800 | 470 | 767 | 1017 | 1236 | 1523
2000 | 422 | 523 | 675 | 744 | 872 |  | 2000 | 464 | 617 | 816 | 886 | 1063 |  | 2000 | 514 | 760 | 910 | 1058 | 1243 | 2000 | 530 | 866 | 1148 | 1395 | 1719
2200 | 470 | 582 | 751 | 828 | 971 |  | 2200 | 517 | 687 | 909 | 987 | 1184 |  | 2200 | 572 | 846 | 1014 | 1178 | 1384 | 2200 | 590 | 964 | 1278 | 1553 | 1914
2400 | 518 | 641 | 828 | 912 | 1070 |  | 2400 | 570 | 757 | 1002 | 1088 | 1305 |  | 2400 | 630 | 932 | 1117 | 1298 | 1525 | 2400 | 650 | 1062 | 1408 | 1711 | 2109
2500 | 542 | 671 | 866 | 955 | 1120 |  | 2500 | 596 | 792 | 1048 | 1138 | 1365 |  | 2500 | 660 | 975 | 1169 | 1358 | 1596 | 2500 | 680 | 1112 | 1474 | 1791 | 2207
2600 | 566 | 701 | 905 | 997 | 1169 |  | 2600 | 623 | 827 | 1095 | 1188 | 1426 |  | 2600 | 689 | 1019 | 1220 | 1418 | 1666 | 2600 | 710 | 1161 | 1539 | 1870 | 2305
2700 | 590 | 730 | 943 | 1039 | 1219 |  | 2700 | 649 | 862 | 1141 | 1239 | 1486 |  | 2700 | 718 | 1062 | 1272 | 1479 | 1737 | 2700 | 741 | 1210 | 1604 | 1949 | 2402
2800 | 614 | 760 | 981 | 1081 | 1268 |  | 2800 | 675 | 897 | 1187 | 1289 | 1546 |  | 2800 | 747 | 1105 | 1324 | 1539 | 1808 | 2800 | 771 | 1259 | 1669 | 2028 | 2500
2900 | 638 | 790 | 1019 | 1124 | 1318 |  | 2900 | 702 | 932 | 1234 | 1340 | 1607 |  | 2900 | 776 | 1148 | 1376 | 1599 | 1878 | 2900 | 801 | 1308 | 1734 | 2108 | 2598
3000 | 662 | 820 | 1058 | 1166 | 1367 |  | 3000 | 728 | 967 | 1280 | 1390 | 1667 |  | 3000 | 805 | 1191 | 1427 | 1659 | 1949 | 3000 | 831 | 1357 | 1800 | 2187 | 2695
3200 | 710 | 879 | 1134 | 1250 | 1466 |  | 3200 | 781 | 1038 | 1373 | 1491 | 1788 |  | 3200 | 864 | 1278 | 1531 | 1779 | 2090 | 3200 | 891 | 1456 | 1930 | 2345 | 2891
3400 | 758 | 938 | 1211 | 1335 | 1565 |  | 3400 | 834 | 1108 | 1466 | 1591 | 1909 |  | 3400 | 922 | 1364 | 1634 | 1899 | 2231 | 3400 | 951 | 1554 | 2060 | 2504 | 3086
3600 | 806 | 998 | 1288 | 1419 | 1665 |  | 3600 | 886 | 1178 | 1558 | 1692 | 2030 |  | 3600 | 981 | 1450 | 1738 | 2019 | 2373 | 3600 | 1011 | 1653 | 2191 | 2662 | 3281
Reynolds numbers at Twater=70 and (Tflow-Trtn) according to calculation values
FMS 90 | [6 empty] | FMS 110 | [6 empty] | FMS 140 | [5 empty] | FMS 190
Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  | Length |  |  | Width B, mm
Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 | Lc, mm | 200 | 250 | 300 | 340 | 420
700 | 514.053 | 640.2297 | 822.4848 | 906.6026 | 1065.4917 |  | 700 | 565.4583 | 752.3867 | 995.3936 | 1084.1845 | 1299.1522 |  | 700 | 626.21 | 929.9686 | 1112.2238 | 1289.8057 | 1518.793 | 700 | 644.9029 | 1056.1453 | 1401.9628 | 1701.0481 | 2098.2709
800 | 626.21 | 775.7527 | 1004.74 | 1107.5506 | 1294.4789 |  | 800 | 691.635 | 915.949 | 1215.0344 | 1317.845 | 1579.5447 |  | 800 | 761.7331 | 1130.9166 | 1355.2307 | 1574.8715 | 1845.9176 | 800 | 789.7724 | 1285.1325 | 1705.7214 | 2074.9049 | 2556.2454
900 | 738.3671 | 915.949 | 1182.3219 | 1303.8254 | 1528.1394 |  | 900 | 813.1384 | 1079.5113 | 1430.002 | 1551.5055 | 1864.6105 |  | 900 | 901.9294 | 1331.8646 | 1593.5643 | 1855.2641 | 2177.7155 | 900 | 929.9686 | 1518.793 | 2009.48 | 2444.0884 | 3014.2199
1000 | 850.5241 | 1056.1453 | 1359.9039 | 1500.1002 | 1761.7999 |  | 1000 | 934.6418 | 1243.0736 | 1649.6428 | 1789.8391 | 2145.003 |  | 1000 | 1037.4524 | 1532.8126 | 1836.5712 | 2135.6566 | 2509.5133 | 1000 | 1070.1649 | 1747.7802 | 2317.9118 | 2813.2719 | 3467.5212
1100 | 962.6811 | 1191.6683 | 1542.159 | 1696.3749 | 1990.7871 |  | 1100 | 1060.8185 | 1406.636 | 1864.6105 | 2023.4996 | 2430.0688 |  | 1100 | 1172.9755 | 1733.7606 | 2079.5781 | 2416.0492 | 2836.638 | 1100 | 1210.3612 | 1976.7675 | 2621.6704 | 3182.4555 | 3925.4957
1200 | 1074.8381 | 1331.8646 | 1719.741 | 1897.3229 | 2224.4476 |  | 1200 | 1182.3219 | 1570.1983 | 2079.5781 | 2257.16 | 2710.4613 |  | 1200 | 1308.4986 | 1934.7086 | 2317.9118 | 2696.4417 | 3168.4358 | 1200 | 1350.5575 | 2205.7547 | 2925.429 | 3556.3122 | 4378.797
1300 | 1186.9951 | 1472.0609 | 1897.3229 | 2093.5977 | 2453.4348 |  | 1300 | 1308.4986 | 1738.4338 | 2299.2189 | 2495.4937 | 2990.8539 |  | 1300 | 1444.0216 | 2140.3298 | 2560.9186 | 2976.8343 | 3495.5605 | 1300 | 1490.7537 | 2434.742 | 3229.1876 | 3925.4957 | 4836.7715
1400 | 1299.1522 | 1607.584 | 2079.5781 | 2289.8725 | 2687.0953 |  | 1400 | 1430.002 | 1901.9961 | 2514.1866 | 2729.1542 | 3275.9197 |  | 1400 | 1584.2179 | 2341.2778 | 2803.9255 | 3257.2268 | 3827.3583 | 1400 | 1630.95 | 2668.4025 | 3532.9462 | 4294.6793 | 5294.746
1500 | 1411.3092 | 1747.7802 | 2257.16 | 2486.1473 | 2916.0825 |  | 1500 | 1551.5055 | 2065.5585 | 2729.1542 | 2967.4878 | 3556.3122 |  | 1500 | 1719.741 | 2542.2258 | 3046.9324 | 3537.6194 | 4159.1562 | 1500 | 1771.1463 | 2897.3897 | 3841.378 | 4663.8628 | 5748.0473
1600 | 1523.4662 | 1887.9765 | 2434.742 | 2687.0953 | 3149.743 |  | 1600 | 1677.6821 | 2229.1208 | 2948.795 | 3201.1483 | 3841.378 |  | 1600 | 1855.2641 | 2743.1738 | 3285.2661 | 3818.0119 | 4486.2808 | 1600 | 1911.3426 | 3126.377 | 4145.1366 | 5037.7195 | 6206.0218
1800 | 1747.7802 | 2163.6959 | 2794.5791 | 3079.6449 | 3612.3907 |  | 1800 | 1920.689 | 2556.2454 | 3383.4035 | 3673.1424 | 4402.1631 |  | 1800 | 2126.3102 | 3145.0698 | 3771.2798 | 4383.4702 | 5149.8765 | 1800 | 2196.4083 | 3584.3515 | 4752.6538 | 5776.0866 | 7117.2976
2000 | 1972.0943 | 2444.0884 | 3154.4162 | 3476.8676 | 4075.0384 |  | 2000 | 2168.3691 | 2883.3701 | 3813.3387 | 4140.4634 | 4967.6214 |  | 2000 | 2402.0295 | 3551.639 | 4252.6204 | 4944.2553 | 5808.799 | 2000 | 2476.8009 | 4046.9992 | 5364.8442 | 6519.1268 | 8033.2466
2200 | 2196.4083 | 2719.8078 | 3509.5801 | 3869.4172 | 4537.6861 |  | 2200 | 2416.0492 | 3210.4947 | 4247.9472 | 4612.4575 | 5533.0797 |  | 2200 | 2673.0757 | 3953.535 | 4738.6341 | 5505.0404 | 6467.7215 | 2200 | 2757.1934 | 4504.9737 | 5972.3614 | 7257.4939 | 8944.5224
2400 | 2420.7224 | 2995.5271 | 3869.4172 | 4261.9668 | 5000.3338 |  | 2400 | 2663.7292 | 3537.6194 | 4682.5556 | 5084.4516 | 6098.538 |  | 2400 | 2944.1218 | 4355.431 | 5219.9747 | 6065.8255 | 7126.644 | 2400 | 3037.586 | 4962.9482 | 6579.8786 | 7995.8609 | 9855.7982
2500 | 2532.8794 | 3135.7234 | 4046.9992 | 4462.9148 | 5233.9943 |  | 2500 | 2785.2327 | 3701.1817 | 4897.5232 | 5318.1121 | 6378.9306 |  | 2500 | 3084.3181 | 4556.379 | 5462.9816 | 6346.2181 | 7458.4419 | 2500 | 3177.7823 | 5196.6086 | 6888.3104 | 8369.7177 | 10313.7727
2600 | 2645.0364 | 3275.9197 | 4229.2543 | 4659.1896 | 5462.9816 |  | 2600 | 2911.4093 | 3864.744 | 5117.1641 | 5551.7725 | 6663.9963 |  | 2600 | 3219.8411 | 4762.0002 | 5701.3152 | 6626.6106 | 7785.5665 | 2600 | 3317.9785 | 5425.5959 | 7192.069 | 8738.9012 | 10771.7472
2700 | 2757.1934 | 3411.4427 | 4406.8363 | 4855.4644 | 5696.642 |  | 2700 | 3032.9128 | 4028.3063 | 5332.1317 | 5790.1062 | 6944.3889 |  | 2700 | 3355.3642 | 4962.9482 | 5944.3221 | 6911.6764 | 8117.3644 | 2700 | 3462.848 | 5654.5831 | 7495.8276 | 9108.0847 | 11225.0485
2800 | 2869.3504 | 3551.639 | 4584.4182 | 5051.7391 | 5925.6293 |  | 2800 | 3154.4162 | 4191.8687 | 5547.0993 | 6023.7667 | 7224.7814 |  | 2800 | 3490.8873 | 5163.8962 | 6187.329 | 7192.069 | 8449.1622 | 2800 | 3603.0443 | 5883.5704 | 7799.5862 | 9477.2683 | 11683.023
2900 | 2981.5075 | 3691.8353 | 4762.0002 | 5252.6871 | 6159.2897 |  | 2900 | 3280.5929 | 4355.431 | 5766.7402 | 6262.1003 | 7509.8472 |  | 2900 | 3626.4103 | 5364.8442 | 6430.3359 | 7472.4615 | 8776.2869 | 2900 | 3743.2406 | 6112.5576 | 8103.3448 | 9851.125 | 12140.9975
3000 | 3093.6645 | 3832.0315 | 4944.2553 | 5448.9619 | 6388.277 |  | 3000 | 3402.0963 | 4518.9933 | 5981.7078 | 6495.7608 | 7790.2397 |  | 3000 | 3761.9334 | 5565.7922 | 6668.6695 | 7752.8541 | 9108.0847 | 3000 | 3883.4368 | 6341.5449 | 8411.7766 | 10220.3085 | 12594.2988
3200 | 3317.9785 | 4107.7509 | 5299.4192 | 5841.5115 | 6850.9247 |  | 3200 | 3649.7764 | 4850.7912 | 6416.3162 | 6967.7549 | 8355.6981 |  | 3200 | 4037.6527 | 5972.3614 | 7154.6833 | 8313.6392 | 9767.0072 | 3200 | 4163.8294 | 6804.1926 | 9019.2938 | 10958.6756 | 13510.2478
3400 | 3542.2926 | 4383.4702 | 5659.2563 | 6238.7343 | 7313.5724 |  | 3400 | 3897.4565 | 5177.9158 | 6850.9247 | 7435.0758 | 8921.1564 |  | 3400 | 4308.6989 | 6374.2574 | 7636.0238 | 8874.4243 | 10425.9297 | 3400 | 4444.222 | 7262.1671 | 9626.811 | 11701.7158 | 14421.5236
3600 | 3766.6066 | 4663.8628 | 6019.0935 | 6631.2839 | 7780.8933 |  | 3600 | 4140.4634 | 5505.0404 | 7280.8599 | 7907.07 | 9486.6147 |  | 3600 | 4584.4182 | 6776.1533 | 8122.0376 | 9435.2094 | 11089.5254 | 3600 | 4724.6145 | 7724.8148 | 10239.0014 | 12440.0829 | 15332.7994
Reynolds numbers at calculation conditions
FMS 90 | [6 empty] | FMS 110 | [6 empty] | FMS 140 | [5 empty] | FMS 190
Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  | Length |  |  | Width B, mm
Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 | Lc, mm | 200 | 250 | 300 | 340 | 420
700 | 514.053 | 640.2297 | 822.4848 | 906.6026 | 1065.4917 |  | 700 | 565.4583 | 752.3867 | 995.3936 | 1084.1845 | 1299.1522 |  | 700 | 626.21 | 929.9686 | 1112.2238 | 1289.8057 | 1518.793 | 700 | 644.9029 | 1056.1453 | 1401.9628 | 1701.0481 | 2098.2709
800 | 626.21 | 775.7527 | 1004.74 | 1107.5506 | 1294.4789 |  | 800 | 691.635 | 915.949 | 1215.0344 | 1317.845 | 1579.5447 |  | 800 | 761.7331 | 1130.9166 | 1355.2307 | 1574.8715 | 1845.9176 | 800 | 789.7724 | 1285.1325 | 1705.7214 | 2074.9049 | 2556.2454
900 | 738.3671 | 915.949 | 1182.3219 | 1303.8254 | 1528.1394 |  | 900 | 813.1384 | 1079.5113 | 1430.002 | 1551.5055 | 1864.6105 |  | 900 | 901.9294 | 1331.8646 | 1593.5643 | 1855.2641 | 2177.7155 | 900 | 929.9686 | 1518.793 | 2009.48 | 2444.0884 | 3014.2199
1000 | 850.5241 | 1056.1453 | 1359.9039 | 1500.1002 | 1761.7999 |  | 1000 | 934.6418 | 1243.0736 | 1649.6428 | 1789.8391 | 2145.003 |  | 1000 | 1037.4524 | 1532.8126 | 1836.5712 | 2135.6566 | 2509.5133 | 1000 | 1070.1649 | 1747.7802 | 2317.9118 | 2813.2719 | 3467.5212
1100 | 962.6811 | 1191.6683 | 1542.159 | 1696.3749 | 1990.7871 |  | 1100 | 1060.8185 | 1406.636 | 1864.6105 | 2023.4996 | 2430.0688 |  | 1100 | 1172.9755 | 1733.7606 | 2079.5781 | 2416.0492 | 2836.638 | 1100 | 1210.3612 | 1976.7675 | 2621.6704 | 3182.4555 | 3925.4957
1200 | 1074.8381 | 1331.8646 | 1719.741 | 1897.3229 | 2224.4476 |  | 1200 | 1182.3219 | 1570.1983 | 2079.5781 | 2257.16 | 2710.4613 |  | 1200 | 1308.4986 | 1934.7086 | 2317.9118 | 2696.4417 | 3168.4358 | 1200 | 1350.5575 | 2205.7547 | 2925.429 | 3556.3122 | 4378.797
1300 | 1186.9951 | 1472.0609 | 1897.3229 | 2093.5977 | 2453.4348 |  | 1300 | 1308.4986 | 1738.4338 | 2299.2189 | 2495.4937 | 2990.8539 |  | 1300 | 1444.0216 | 2140.3298 | 2560.9186 | 2976.8343 | 3495.5605 | 1300 | 1490.7537 | 2434.742 | 3229.1876 | 3925.4957 | 4836.7715
1400 | 1299.1522 | 1607.584 | 2079.5781 | 2289.8725 | 2687.0953 |  | 1400 | 1430.002 | 1901.9961 | 2514.1866 | 2729.1542 | 3275.9197 |  | 1400 | 1584.2179 | 2341.2778 | 2803.9255 | 3257.2268 | 3827.3583 | 1400 | 1630.95 | 2668.4025 | 3532.9462 | 4294.6793 | 5294.746
1500 | 1411.3092 | 1747.7802 | 2257.16 | 2486.1473 | 2916.0825 |  | 1500 | 1551.5055 | 2065.5585 | 2729.1542 | 2967.4878 | 3556.3122 |  | 1500 | 1719.741 | 2542.2258 | 3046.9324 | 3537.6194 | 4159.1562 | 1500 | 1771.1463 | 2897.3897 | 3841.378 | 4663.8628 | 5748.0473
1600 | 1523.4662 | 1887.9765 | 2434.742 | 2687.0953 | 3149.743 |  | 1600 | 1677.6821 | 2229.1208 | 2948.795 | 3201.1483 | 3841.378 |  | 1600 | 1855.2641 | 2743.1738 | 3285.2661 | 3818.0119 | 4486.2808 | 1600 | 1911.3426 | 3126.377 | 4145.1366 | 5037.7195 | 6206.0218
1800 | 1747.7802 | 2163.6959 | 2794.5791 | 3079.6449 | 3612.3907 |  | 1800 | 1920.689 | 2556.2454 | 3383.4035 | 3673.1424 | 4402.1631 |  | 1800 | 2126.3102 | 3145.0698 | 3771.2798 | 4383.4702 | 5149.8765 | 1800 | 2196.4083 | 3584.3515 | 4752.6538 | 5776.0866 | 7117.2976
2000 | 1972.0943 | 2444.0884 | 3154.4162 | 3476.8676 | 4075.0384 |  | 2000 | 2168.3691 | 2883.3701 | 3813.3387 | 4140.4634 | 4967.6214 |  | 2000 | 2402.0295 | 3551.639 | 4252.6204 | 4944.2553 | 5808.799 | 2000 | 2476.8009 | 4046.9992 | 5364.8442 | 6519.1268 | 8033.2466
2200 | 2196.4083 | 2719.8078 | 3509.5801 | 3869.4172 | 4537.6861 |  | 2200 | 2416.0492 | 3210.4947 | 4247.9472 | 4612.4575 | 5533.0797 |  | 2200 | 2673.0757 | 3953.535 | 4738.6341 | 5505.0404 | 6467.7215 | 2200 | 2757.1934 | 4504.9737 | 5972.3614 | 7257.4939 | 8944.5224
2400 | 2420.7224 | 2995.5271 | 3869.4172 | 4261.9668 | 5000.3338 |  | 2400 | 2663.7292 | 3537.6194 | 4682.5556 | 5084.4516 | 6098.538 |  | 2400 | 2944.1218 | 4355.431 | 5219.9747 | 6065.8255 | 7126.644 | 2400 | 3037.586 | 4962.9482 | 6579.8786 | 7995.8609 | 9855.7982
2500 | 2532.8794 | 3135.7234 | 4046.9992 | 4462.9148 | 5233.9943 |  | 2500 | 2785.2327 | 3701.1817 | 4897.5232 | 5318.1121 | 6378.9306 |  | 2500 | 3084.3181 | 4556.379 | 5462.9816 | 6346.2181 | 7458.4419 | 2500 | 3177.7823 | 5196.6086 | 6888.3104 | 8369.7177 | 10313.7727
2600 | 2645.0364 | 3275.9197 | 4229.2543 | 4659.1896 | 5462.9816 |  | 2600 | 2911.4093 | 3864.744 | 5117.1641 | 5551.7725 | 6663.9963 |  | 2600 | 3219.8411 | 4762.0002 | 5701.3152 | 6626.6106 | 7785.5665 | 2600 | 3317.9785 | 5425.5959 | 7192.069 | 8738.9012 | 10771.7472
2700 | 2757.1934 | 3411.4427 | 4406.8363 | 4855.4644 | 5696.642 |  | 2700 | 3032.9128 | 4028.3063 | 5332.1317 | 5790.1062 | 6944.3889 |  | 2700 | 3355.3642 | 4962.9482 | 5944.3221 | 6911.6764 | 8117.3644 | 2700 | 3462.848 | 5654.5831 | 7495.8276 | 9108.0847 | 11225.0485
2800 | 2869.3504 | 3551.639 | 4584.4182 | 5051.7391 | 5925.6293 |  | 2800 | 3154.4162 | 4191.8687 | 5547.0993 | 6023.7667 | 7224.7814 |  | 2800 | 3490.8873 | 5163.8962 | 6187.329 | 7192.069 | 8449.1622 | 2800 | 3603.0443 | 5883.5704 | 7799.5862 | 9477.2683 | 11683.023
2900 | 2981.5075 | 3691.8353 | 4762.0002 | 5252.6871 | 6159.2897 |  | 2900 | 3280.5929 | 4355.431 | 5766.7402 | 6262.1003 | 7509.8472 |  | 2900 | 3626.4103 | 5364.8442 | 6430.3359 | 7472.4615 | 8776.2869 | 2900 | 3743.2406 | 6112.5576 | 8103.3448 | 9851.125 | 12140.9975
3000 | 3093.6645 | 3832.0315 | 4944.2553 | 5448.9619 | 6388.277 |  | 3000 | 3402.0963 | 4518.9933 | 5981.7078 | 6495.7608 | 7790.2397 |  | 3000 | 3761.9334 | 5565.7922 | 6668.6695 | 7752.8541 | 9108.0847 | 3000 | 3883.4368 | 6341.5449 | 8411.7766 | 10220.3085 | 12594.2988
3200 | 3317.9785 | 4107.7509 | 5299.4192 | 5841.5115 | 6850.9247 |  | 3200 | 3649.7764 | 4850.7912 | 6416.3162 | 6967.7549 | 8355.6981 |  | 3200 | 4037.6527 | 5972.3614 | 7154.6833 | 8313.6392 | 9767.0072 | 3200 | 4163.8294 | 6804.1926 | 9019.2938 | 10958.6756 | 13510.2478
3400 | 3542.2926 | 4383.4702 | 5659.2563 | 6238.7343 | 7313.5724 |  | 3400 | 3897.4565 | 5177.9158 | 6850.9247 | 7435.0758 | 8921.1564 |  | 3400 | 4308.6989 | 6374.2574 | 7636.0238 | 8874.4243 | 10425.9297 | 3400 | 4444.222 | 7262.1671 | 9626.811 | 11701.7158 | 14421.5236
3600 | 3766.6066 | 4663.8628 | 6019.0935 | 6631.2839 | 7780.8933 |  | 3600 | 4140.4634 | 5505.0404 | 7280.8599 | 7907.07 | 9486.6147 |  | 3600 | 4584.4182 | 6776.1533 | 8122.0376 | 9435.2094 | 11089.5254 | 3600 | 4724.6145 | 7724.8148 | 10239.0014 | 12440.0829 | 15332.7994
Re corrected heat outputs in Watts
FMS 90 | [6 empty] | FMS 110 | [6 empty] | FMS 140 | [5 empty] | FMS 190
Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  | Length |  |  | Width B, mm
Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 | Lc, mm | 200 | 250 | 300 | 340 | 420
700 | 110 | 137 | 176 | 194 | 228 |  | 700 | 121 | 161 | 213 | 232 | 278 |  | 700 | 134 | 199 | 238 | 276 | 325 | 700 | 138 | 226 | 300 | 364 | 449
800 | 134 | 166 | 215 | 237 | 277 |  | 800 | 148 | 196 | 260 | 282 | 338 |  | 800 | 163 | 242 | 290 | 337 | 395 | 800 | 169 | 275 | 365 | 444 | 547
900 | 158 | 196 | 253 | 279 | 327 |  | 900 | 174 | 231 | 306 | 332 | 399 |  | 900 | 193 | 285 | 341 | 397 | 466 | 900 | 199 | 325 | 430 | 523 | 645
1000 | 182 | 226 | 291 | 321 | 377 |  | 1000 | 200 | 266 | 353 | 383 | 459 |  | 1000 | 222 | 328 | 393 | 457 | 537 | 1000 | 229 | 374 | 496 | 602 | 742
1100 | 206 | 255 | 330 | 363 | 426 |  | 1100 | 227 | 301 | 399 | 433 | 520 |  | 1100 | 251 | 371 | 445 | 517 | 607 | 1100 | 259 | 423 | 561 | 681 | 840
1200 | 230 | 285 | 368 | 406 | 476 |  | 1200 | 253 | 336 | 445 | 483 | 580 |  | 1200 | 280 | 414 | 496 | 577 | 678 | 1200 | 289 | 472 | 626 | 761 | 937
1300 | 254 | 315 | 406 | 448 | 525 |  | 1300 | 280 | 372 | 492 | 534 | 640 |  | 1300 | 309 | 458 | 548 | 637 | 748 | 1300 | 319 | 521 | 691 | 840 | 1035
1400 | 278 | 344 | 445 | 490 | 575 |  | 1400 | 306 | 407 | 538 | 584 | 701 |  | 1400 | 339 | 501 | 600 | 697 | 819 | 1400 | 349 | 571 | 756 | 919 | 1133
1500 | 302 | 374 | 483 | 532 | 624 |  | 1500 | 332 | 442 | 584 | 635 | 761 |  | 1500 | 368 | 544 | 652 | 757 | 890 | 1500 | 379 | 620 | 822 | 998 | 1230
1600 | 326 | 404 | 521 | 575 | 674 |  | 1600 | 359 | 477 | 631 | 685 | 822 |  | 1600 | 397 | 587 | 703 | 817 | 960 | 1600 | 409 | 669 | 887 | 1078 | 1328
1800 | 374 | 463 | 598 | 659 | 773 |  | 1800 | 411 | 547 | 724 | 786 | 942 |  | 1800 | 455 | 673 | 807 | 938 | 1102 | 1800 | 470 | 767 | 1017 | 1236 | 1523
2000 | 422 | 523 | 675 | 744 | 872 |  | 2000 | 464 | 617 | 816 | 886 | 1063 |  | 2000 | 514 | 760 | 910 | 1058 | 1243 | 2000 | 530 | 866 | 1148 | 1395 | 1719
2200 | 470 | 582 | 751 | 828 | 971 |  | 2200 | 517 | 687 | 909 | 987 | 1184 |  | 2200 | 572 | 846 | 1014 | 1178 | 1384 | 2200 | 590 | 964 | 1278 | 1553 | 1914
2400 | 518 | 641 | 828 | 912 | 1070 |  | 2400 | 570 | 757 | 1002 | 1088 | 1305 |  | 2400 | 630 | 932 | 1117 | 1298 | 1525 | 2400 | 650 | 1062 | 1408 | 1711 | 2109
2500 | 542 | 671 | 866 | 955 | 1120 |  | 2500 | 596 | 792 | 1048 | 1138 | 1365 |  | 2500 | 660 | 975 | 1169 | 1358 | 1596 | 2500 | 680 | 1112 | 1474 | 1791 | 2207
2600 | 566 | 701 | 905 | 997 | 1169 |  | 2600 | 623 | 827 | 1095 | 1188 | 1426 |  | 2600 | 689 | 1019 | 1220 | 1418 | 1666 | 2600 | 710 | 1161 | 1539 | 1870 | 2305
2700 | 590 | 730 | 943 | 1039 | 1219 |  | 2700 | 649 | 862 | 1141 | 1239 | 1486 |  | 2700 | 718 | 1062 | 1272 | 1479 | 1737 | 2700 | 741 | 1210 | 1604 | 1949 | 2402
2800 | 614 | 760 | 981 | 1081 | 1268 |  | 2800 | 675 | 897 | 1187 | 1289 | 1546 |  | 2800 | 747 | 1105 | 1324 | 1539 | 1808 | 2800 | 771 | 1259 | 1669 | 2028 | 2500
2900 | 638 | 790 | 1019 | 1124 | 1318 |  | 2900 | 702 | 932 | 1234 | 1340 | 1607 |  | 2900 | 776 | 1148 | 1376 | 1599 | 1878 | 2900 | 801 | 1308 | 1734 | 2108 | 2598
3000 | 662 | 820 | 1058 | 1166 | 1367 |  | 3000 | 728 | 967 | 1280 | 1390 | 1667 |  | 3000 | 805 | 1191 | 1427 | 1659 | 1949 | 3000 | 831 | 1357 | 1800 | 2187 | 2695
3200 | 710 | 879 | 1134 | 1250 | 1466 |  | 3200 | 781 | 1038 | 1373 | 1491 | 1788 |  | 3200 | 864 | 1278 | 1531 | 1779 | 2090 | 3200 | 891 | 1456 | 1930 | 2345 | 2891
3400 | 758 | 938 | 1211 | 1335 | 1565 |  | 3400 | 834 | 1108 | 1466 | 1591 | 1909 |  | 3400 | 922 | 1364 | 1634 | 1899 | 2231 | 3400 | 951 | 1554 | 2060 | 2504 | 3086
3600 | 806 | 998 | 1288 | 1419 | 1665 |  | 3600 | 886 | 1178 | 1558 | 1692 | 2030 |  | 3600 | 981 | 1450 | 1738 | 2019 | 2373 | 3600 | 1011 | 1653 | 2191 | 2662 | 3281
Flow resistance / Pressure drop in Pascals
FMS 90 | [6 empty] | FMS 110 | [6 empty] | FMS 140 | [5 empty] | FMS 190
Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  | Length |  |  | Width B, mm
Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 | Lc, mm | 200 | 250 | 300 | 340 | 420
700 | 0.41153 | 0.61101 | 9.2255 | 11.0276 | 2.9055 |  | 700 | 0.48858 | 0.81712 | 13.0869 | 15.3051 | 4.1695 |  | 700 | 1.1035 | 2.2678 | 10.2762 | 13.2605 | 19.4913 | 700 | 1.1642 | 2.8593 | 15.3069 | 21.3517 | 34.802
800 | 0.74553 | 1.0961 | 16.5739 | 19.8003 | 5.532 |  | 800 | 0.89153 | 1.478 | 23.4483 | 27.1967 | 7.9446 |  | 800 | 2.1091 | 4.3271 | 14.5533 | 18.8944 | 28.9992 | 800 | 2.2524 | 5.4596 | 21.7058 | 30.5111 | 52.0922
900 | 1.2147 | 1.79 | 26.5222 | 31.6888 | 9.3189 |  | 900 | 1.4449 | 2.4054 | 37.4884 | 43.4845 | 13.3743 |  | 900 | 3.5779 | 7.2606 | 19.6394 | 25.639 | 41.403 | 900 | 3.7824 | 9.2157 | 29.4916 | 41.5696 | 74.4191
1000 | 1.8382 | 2.7131 | 39.4387 | 47.1194 | 14.3909 |  | 1000 | 2.1779 | 3.6366 | 55.9812 | 64.9059 | 20.5591 |  | 1000 | 5.511 | 11.1812 | 25.9311 | 33.8525 | 57.2293 | 1000 | 5.83 | 14.184 | 39.1227 | 55.0867 | 102.6737
1100 | 2.6341 | 3.865 | 55.8702 | 66.3767 | 20.7901 |  | 1100 | 3.1361 | 5.2068 | 78.7518 | 91.2997 | 29.8226 |  | 1100 | 7.9827 | 16.1891 | 33.6223 | 43.9028 | 76.9762 | 1100 | 8.449 | 20.5259 | 50.7688 | 71.6733 | 138.6122
1200 | 3.6195 | 5.3196 | 75.4891 | 90.1201 | 28.7876 |  | 1200 | 4.2952 | 7.1496 | 106.3242 | 123.2499 | 41.1377 |  | 1200 | 11.0384 | 22.3728 | 42.9121 | 56.2525 | 101.855 | 1200 | 11.6876 | 28.3521 | 65.0862 | 92.3123 | 183.089
1300 | 4.8108 | 7.0796 | 98.7502 | 117.8698 | 38.2839 |  | 1300 | 5.7305 | 9.5426 | 139.4936 | 161.6282 | 54.7207 |  | 1300 | 14.7182 | 29.9283 | 54.5083 | 71.4519 | 132.1811 | 1300 | 15.5884 | 37.7595 | 82.7127 | 117.5146 | 238.2167
1400 | 6.2238 | 9.1206 | 126.3681 | 150.1996 | 49.6061 |  | 1400 | 7.393 | 12.3326 | 177.6063 | 205.7598 | 70.8704 |  | 1400 | 19.1596 | 38.7091 | 68.7538 | 90.123 | 169.3642 | 1400 | 20.1892 | 48.9865 | 104.3683 | 148.4936 | 305.139
1500 | 7.8732 | 11.5522 | 157.6098 | 187.3585 | 62.5402 |  | 1500 | 9.3304 | 15.5868 | 221.3835 | 257.163 | 89.3511 |  | 1500 | 24.2068 | 48.8717 | 86.1613 | 112.9311 | 213.9044 | 1500 | 25.5229 | 61.8215 | 131.1105 | 186.3414 | 384.6214
1600 | 9.7734 | 14.3552 | 193.1342 | 230.324 | 77.4847 |  | 1600 | 11.617 | 19.3326 | 271.9012 | 314.84 | 110.6415 |  | 1600 | 29.9729 | 60.4659 | 106.9719 | 140.5447 | 265.9724 | 1600 | 31.6181 | 76.4563 | 163.1772 | 232.5371 | 478.843
1800 | 14.3805 | 21.0741 | 278.8389 | 331.4465 | 112.8803 |  | 1800 | 17.0263 | 28.4038 | 391.8367 | 453.5227 | 160.7653 |  | 1800 | 43.7503 | 88.1087 | 161.9601 | 212.9774 | 396.9457 | 1800 | 46.3632 | 111.3182 | 246.753 | 351.9215 | 712.1551
2000 | 20.1477 | 29.5723 | 385.2449 | 457.8714 | 156.0905 |  | 2000 | 23.8735 | 39.7431 | 539.4256 | 624.2499 | 222.1737 |  | 2000 | 60.8444 | 122.1693 | 235.7098 | 310.009 | 562.6265 | 2000 | 64.2612 | 154.1813 | 359.6201 | 512.5426 | 1007.6662
2200 | 27.1692 | 39.8025 | 513.9813 | 610.9795 | 207.2731 |  | 2200 | 32.2126 | 53.5303 | 720.804 | 833.9524 | 294.8132 |  | 2200 | 80.9636 | 162.2664 | 328.9767 | 431.527 | 760.5785 | 2200 | 85.5446 | 204.6262 | 500.0979 | 711.6274 | 1356.7134
2400 | 35.5313 | 51.9686 | 670.8646 | 795.9412 | 266.4641 |  | 2400 | 42.1458 | 69.9293 | 940.1469 | 1087.5934 | 378.6964 |  | 2400 | 104.3229 | 208.6768 | 436.6939 | 571.8474 | 982.7866 | 2400 | 110.2575 | 262.9473 | 661.775 | 939.0568 | 1744.0559
2500 | 40.2401 | 58.891 | 760.0982 | 903.6936 | 299.2806 |  | 2500 | 47.6685 | 79.1554 | 1065.1464 | 1232.2572 | 424.5411 |  | 2500 | 117.5341 | 234.2396 | 494.0876 | 645.7119 | 1099.73 | 2500 | 123.9018 | 295.5128 | 747.5019 | 1058.5098 | 1945.4303
2600 | 45.3131 | 66.3506 | 859.4864 | 1020.0314 | 333.5929 |  | 2600 | 53.7668 | 89.0892 | 1204.0366 | 1390.7896 | 473.6835 |  | 2600 | 131.2601 | 261.8129 | 551.0392 | 719.6199 | 1216.3615 | 2600 | 138.4007 | 329.5756 | 832.1809 | 1175.8918 | 2146.646
2700 | 50.7592 | 74.179 | 966.568 | 1147.422 | 370.3538 |  | 2700 | 60.1546 | 99.7472 | 1354.1829 | 1566.7145 | 524.9499 |  | 2700 | 145.7886 | 290.5025 | 607.5273 | 792.407 | 1332.9844 | 2700 | 154.1143 | 365.5513 | 914.1914 | 1288.6111 | 2341.9761
2800 | 56.5868 | 82.738 | 1083.7579 | 1286.9068 | 408.4966 |  | 2800 | 66.9842 | 111.1452 | 1518.6264 | 1757.1899 | 578.8454 |  | 2800 | 161.1124 | 320.713 | 661.1082 | 859.9937 | 1446.077 | 2800 | 170.3245 | 403.4122 | 990.9469 | 1392.959 | 2530.5864
2900 | 62.8038 | 91.8705 | 1212.0279 | 1441.9319 | 449.0901 |  | 2900 | 74.4531 | 123.2979 | 1701.211 | 1968.5338 | 636.0137 |  | 2900 | 177.2221 | 352.4206 | 710.0719 | 921.0536 | 1551.8755 | 2900 | 187.3656 | 443.1263 | 1059.875 | 1486.5207 | 2706.6846
3000 | 69.418 | 101.5876 | 1354.7416 | 1609.4548 | 490.9329 |  | 3000 | 82.2049 | 136.2196 | 1898.8265 | 2197.6035 | 695.0447 |  | 3000 | 194.107 | 385.5983 | 751.8744 | 973.4806 | 1650.8857 | 3000 | 205.2258 | 484.6572 | 1119.6277 | 1563.5055 | 2864.4622
3200 | 83.8665 | 122.5693 | 1677.6078 | 1994.4937 | 580.5922 |  | 3200 | 99.3455 | 164.7043 | 2356.3802 | 2728.0865 | 821.2192 |  | 3200 | 230.6163 | 456.8645 | 812.8559 | 1045.3275 | 1814.4497 | 3200 | 243.3477 | 573.6938 | 1198.2049 | 1660.5334 | 3119.802
3400 | 99.9861 | 145.9516 | 2069.247 | 2461.8389 | 677.1077 |  | 3400 | 118.4695 | 196.1663 | 2908.742 | 3365.3703 | 956.814 |  | 3400 | 269.6341 | 533.0455 | 833.8611 | 1065.3267 | 1922.3943 | 3400 | 284.5644 | 668.8469 | 1216.4312 | 1672.0544 | 3269.7758
3600 | 117.8252 | 172.1068 | 2542.7139 | 3023.8277 | 780.8789 |  | 3600 | 139.3545 | 230.9436 | 3574.0955 | 4142.6035 | 1101.2101 |  | 3600 | 311.9969 | 614.397 | 813.8614 | 1031.027 | 1966.9559 | 3600 | 328.7289 | 771.1445 | 1173.0208 | 1595.0241 | 3303.556
Heat output in Watts
Pressure drop in Pascal
FMS 90 | [6 empty] | FMS 110 | [6 empty] | FMS 140 | [5 empty] | FMS 190
Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  | Length |  |  | Width B, mm
Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 | Lc, mm | 200 | 250 | 300 | 340 | 420
700 W | 110 | 137 | 176 | 194 | 228 |  | 700 W | 121 | 161 | 213 | 232 | 278 |  | 700 W | 134 | 199 | 238 | 276 | 325 | 700 W | 138 | 226 | 300 | 364 | 449
Pa | < 25 | < 25 | < 25 | < 25 | < 25 |  | Pa | < 25 | < 25 | < 25 | < 25 | < 25 |  | Pa | < 25 | < 25 | < 25 | < 25 | < 25 | Pa | < 25 | < 25 | < 25 | < 25 | 34.802
800 W | 134 | 166 | 215 | 237 | 277 |  | 800 W | 148 | 196 | 260 | 282 | 338 |  | 800 W | 163 | 242 | 290 | 337 | 395 | 800 W | 169 | 275 | 365 | 444 | 547
Pa | < 25 | < 25 | < 25 | < 25 | < 25 |  | Pa | < 25 | < 25 | < 25 | 27.1967 | < 25 |  | Pa | < 25 | < 25 | < 25 | < 25 | 28.9992 | Pa | < 25 | < 25 | < 25 | 30.5111 | 52.0922
900 W | 158 | 196 | 253 | 279 | 327 |  | 900 W | 174 | 231 | 306 | 332 | 399 |  | 900 W | 193 | 285 | 341 | 397 | 466 | 900 W | 199 | 325 | 430 | 523 | 645
Pa | < 25 | < 25 | 26.5222 | 31.6888 | < 25 |  | Pa | < 25 | < 25 | 37.4884 | 43.4845 | < 25 |  | Pa | < 25 | < 25 | < 25 | 25.639 | 41.403 | Pa | < 25 | < 25 | 29.4916 | 41.5696 | 74.4191
1000 W | 182 | 226 | 291 | 321 | 377 |  | 1000 W | 200 | 266 | 353 | 383 | 459 |  | 1000 W | 222 | 328 | 393 | 457 | 537 | 1000 W | 229 | 374 | 496 | 602 | 742
Pa | < 25 | < 25 | 39.4387 | 47.1194 | < 25 |  | Pa | < 25 | < 25 | 55.9812 | 64.9059 | < 25 |  | Pa | < 25 | < 25 | 25.9311 | 33.8525 | 57.2293 | Pa | < 25 | < 25 | 39.1227 | 55.0867 | 102.6737
1100 W | 206 | 255 | 330 | 363 | 426 |  | 1100 W | 227 | 301 | 399 | 433 | 520 |  | 1100 W | 251 | 371 | 445 | 517 | 607 | 1100 W | 259 | 423 | 561 | 681 | 840
Pa | < 25 | < 25 | 55.8702 | 66.3767 | < 25 |  | Pa | < 25 | < 25 | 78.7518 | 91.2997 | 29.8226 |  | Pa | < 25 | < 25 | 33.6223 | 43.9028 | 76.9762 | Pa | < 25 | < 25 | 50.7688 | 71.6733 | 138.6122
1200 W | 230 | 285 | 368 | 406 | 476 |  | 1200 W | 253 | 336 | 445 | 483 | 580 |  | 1200 W | 280 | 414 | 496 | 577 | 678 | 1200 W | 289 | 472 | 626 | 761 | 937
Pa | < 25 | < 25 | 75.4891 | 90.1201 | 28.7876 |  | Pa | < 25 | < 25 | 106.3242 | 123.2499 | 41.1377 |  | Pa | < 25 | < 25 | 42.9121 | 56.2525 | 101.855 | Pa | < 25 | 28.3521 | 65.0862 | 92.3123 | 183.089
1300 W | 254 | 315 | 406 | 448 | 525 |  | 1300 W | 280 | 372 | 492 | 534 | 640 |  | 1300 W | 309 | 458 | 548 | 637 | 748 | 1300 W | 319 | 521 | 691 | 840 | 1035
Pa | < 25 | < 25 | 98.7502 | 117.8698 | 38.2839 |  | Pa | < 25 | < 25 | 139.4936 | 161.6282 | 54.7207 |  | Pa | < 25 | 29.9283 | 54.5083 | 71.4519 | 132.1811 | Pa | < 25 | 37.7595 | 82.7127 | 117.5146 | 238.2167
1400 W | 278 | 344 | 445 | 490 | 575 |  | 1400 W | 306 | 407 | 538 | 584 | 701 |  | 1400 W | 339 | 501 | 600 | 697 | 819 | 1400 W | 349 | 571 | 756 | 919 | 1133
Pa | < 25 | < 25 | 126.3681 | 150.1996 | 49.6061 |  | Pa | < 25 | < 25 | 177.6063 | 205.7598 | 70.8704 |  | Pa | < 25 | 38.7091 | 68.7538 | 90.123 | 169.3642 | Pa | < 25 | 48.9865 | 104.3683 | 148.4936 | 305.139
1500 W | 302 | 374 | 483 | 532 | 624 |  | 1500 W | 332 | 442 | 584 | 635 | 761 |  | 1500 W | 368 | 544 | 652 | 757 | 890 | 1500 W | 379 | 620 | 822 | 998 | 1230
Pa | < 25 | < 25 | 157.6098 | 187.3585 | 62.5402 |  | Pa | < 25 | < 25 | 221.3835 | 257.163 | 89.3511 |  | Pa | < 25 | 48.8717 | 86.1613 | 112.9311 | 213.9044 | Pa | 25.5229 | 61.8215 | 131.1105 | 186.3414 | 384.6214
1600 W | 326 | 404 | 521 | 575 | 674 |  | 1600 W | 359 | 477 | 631 | 685 | 822 |  | 1600 W | 397 | 587 | 703 | 817 | 960 | 1600 W | 409 | 669 | 887 | 1078 | 1328
Pa | < 25 | < 25 | 193.1342 | 230.324 | 77.4847 |  | Pa | < 25 | < 25 | 271.9012 | 314.84 | 110.6415 |  | Pa | < 25 | < 25 | < 25 | < 25 | < 25 | Pa | 31.6181 | 76.4563 | 163.1772 | 232.5371 | 478.843
1800 W | 374 | 463 | 598 | 659 | 773 |  | 1800 W | 411 | 547 | 724 | 786 | 942 |  | 1800 W | 455 | 673 | 807 | 938 | 1102 | 1800 W | 470 | 767 | 1017 | 1236 | 1523
Pa | < 25 | < 25 | 278.8389 | 331.4465 | 112.8803 |  | Pa | < 25 | 28.4038 | 391.8367 | 453.5227 | 160.7653 |  | Pa | 43.7503 | 88.1087 | 161.9601 | 212.9774 | 396.9457 | Pa | 46.3632 | 111.3182 | 246.753 | 351.9215 | 712.1551
2000 W | 422 | 523 | 675 | 744 | 872 |  | 2000 W | 464 | 617 | 816 | 886 | 1063 |  | 2000 W | 514 | 760 | 910 | 1058 | 1243 | 2000 W | 530 | 866 | 1148 | 1395 | 1719
Pa | < 25 | 29.5723 | 385.2449 | 457.8714 | 156.0905 |  | Pa | < 25 | 39.7431 | 539.4256 | 624.2499 | 222.1737 |  | Pa | 60.8444 | 122.1693 | 235.7098 | 310.009 | 562.6265 | Pa | 64.2612 | 154.1813 | 359.6201 | 512.5426 | 1007.6662
2200 W | 470 | 582 | 751 | 828 | 971 |  | 2200 W | 517 | 687 | 909 | 987 | 1184 |  | 2200 W | 572 | 846 | 1014 | 1178 | 1384 | 2200 W | 590 | 964 | 1278 | 1553 | 1914
Pa | 27.1692 | 39.8025 | 513.9813 | 610.9795 | 207.2731 |  | Pa | 32.2126 | 53.5303 | 720.804 | 833.9524 | 294.8132 |  | Pa | 80.9636 | 162.2664 | 328.9767 | 431.527 | 760.5785 | Pa | 85.5446 | 204.6262 | 500.0979 | 711.6274 | 1356.7134
2400 W | 518 | 641 | 828 | 912 | 1070 |  | 2400 W | 570 | 757 | 1002 | 1088 | 1305 |  | 2400 W | 630 | 932 | 1117 | 1298 | 1525 | 2400 W | 650 | 1062 | 1408 | 1711 | 2109
Pa | 35.5313 | 51.9686 | 670.8646 | 795.9412 | 266.4641 |  | Pa | 42.1458 | 69.9293 | 940.1469 | 1087.5934 | 378.6964 |  | Pa | 104.3229 | 208.6768 | 436.6939 | 571.8474 | 982.7866 | Pa | 110.2575 | 262.9473 | 661.775 | 939.0568 | 1744.0559
2500 W | 542 | 671 | 866 | 955 | 1120 |  | 2500 W | 596 | 792 | 1048 | 1138 | 1365 |  | 2500 W | 660 | 975 | 1169 | 1358 | 1596 | 2500 W | 680 | 1112 | 1474 | 1791 | 2207
Pa | 40.2401 | 58.891 | 760.0982 | 903.6936 | 299.2806 |  | Pa | 47.6685 | 79.1554 | 1065.1464 | 1232.2572 | 424.5411 |  | Pa | 117.5341 | 234.2396 | 494.0876 | 645.7119 | 1099.73 | Pa | 123.9018 | 295.5128 | 747.5019 | 1058.5098 | 1945.4303
2600 W | 566 | 701 | 905 | 997 | 1169 |  | 2600 W | 623 | 827 | 1095 | 1188 | 1426 |  | 2600 W | 689 | 1019 | 1220 | 1418 | 1666 | 2600 W | 710 | 1161 | 1539 | 1870 | 2305
Pa | 45.3131 | 66.3506 | 859.4864 | 1020.0314 | 333.5929 |  | Pa | 53.7668 | 89.0892 | 1204.0366 | 1390.7896 | 473.6835 |  | Pa | 131.2601 | 261.8129 | 551.0392 | 719.6199 | 1216.3615 | Pa | 138.4007 | 329.5756 | 832.1809 | 1175.8918 | 2146.646
2700 W | 590 | 730 | 943 | 1039 | 1219 |  | 2700 W | 649 | 862 | 1141 | 1239 | 1486 |  | 2700 W | 718 | 1062 | 1272 | 1479 | 1737 | 2700 W | 741 | 1210 | 1604 | 1949 | 2402
Pa | 50.7592 | 74.179 | 966.568 | 1147.422 | 370.3538 |  | Pa | 60.1546 | 99.7472 | 1354.1829 | 1566.7145 | 524.9499 |  | Pa | 145.7886 | 290.5025 | 607.5273 | 792.407 | 1332.9844 | Pa | 154.1143 | 365.5513 | 914.1914 | 1288.6111 | 2341.9761
2800 W | 614 | 760 | 981 | 1081 | 1268 |  | 2800 W | 675 | 897 | 1187 | 1289 | 1546 |  | 2800 W | 747 | 1105 | 1324 | 1539 | 1808 | 2800 W | 771 | 1259 | 1669 | 2028 | 2500
Pa | 56.5868 | 82.738 | 1083.7579 | 1286.9068 | 408.4966 |  | Pa | 66.9842 | 111.1452 | 1518.6264 | 1757.1899 | 578.8454 |  | Pa | 161.1124 | 320.713 | 661.1082 | 859.9937 | 1446.077 | Pa | 170.3245 | 403.4122 | 990.9469 | 1392.959 | 2530.5864
2900 W | 638 | 790 | 1019 | 1124 | 1318 |  | 2900 W | 702 | 932 | 1234 | 1340 | 1607 |  | 2900 W | 776 | 1148 | 1376 | 1599 | 1878 | 2900 W | 801 | 1308 | 1734 | 2108 | 2598
Pa | 62.8038 | 91.8705 | 1212.0279 | 1441.9319 | 449.0901 |  | Pa | 74.4531 | 123.2979 | 1701.211 | 1968.5338 | 636.0137 |  | Pa | 177.2221 | 352.4206 | 710.0719 | 921.0536 | 1551.8755 | Pa | 187.3656 | 443.1263 | 1059.875 | 1486.5207 | 2706.6846
3000 W | 662 | 820 | 1058 | 1166 | 1367 |  | 3000 W | 728 | 967 | 1280 | 1390 | 1667 |  | 3000 W | 805 | 1191 | 1427 | 1659 | 1949 | 3000 W | 831 | 1357 | 1800 | 2187 | 2695
Pa | 69.418 | 101.5876 | 1354.7416 | 1609.4548 | 490.9329 |  | Pa | 82.2049 | 136.2196 | 1898.8265 | 2197.6035 | 695.0447 |  | Pa | 194.107 | 385.5983 | 751.8744 | 973.4806 | 1650.8857 | Pa | 205.2258 | 484.6572 | 1119.6277 | 1563.5055 | 2864.4622
3200 W | 710 | 879 | 1134 | 1250 | 1466 |  | 3200 W | 781 | 1038 | 1373 | 1491 | 1788 |  | 3200 W | 864 | 1278 | 1531 | 1779 | 2090 | 3200 W | 891 | 1456 | 1930 | 2345 | 2891
Pa | 83.8665 | 122.5693 | 1677.6078 | 1994.4937 | 580.5922 |  | Pa | 99.3455 | 164.7043 | 2356.3802 | 2728.0865 | 821.2192 |  | Pa | 230.6163 | 456.8645 | 812.8559 | 1045.3275 | 1814.4497 | Pa | 243.3477 | 573.6938 | 1198.2049 | 1660.5334 | 3119.802
3400 W | 758 | 938 | 1211 | 1335 | 1565 |  | 3400 W | 834 | 1108 | 1466 | 1591 | 1909 |  | 3400 W | 922 | 1364 | 1634 | 1899 | 2231 | 3400 W | 951 | 1554 | 2060 | 2504 | 3086
Pa | 99.9861 | 145.9516 | 2069.247 | 2461.8389 | 677.1077 |  | Pa | 118.4695 | 196.1663 | 2908.742 | 3365.3703 | 956.814 |  | Pa | 269.6341 | 533.0455 | 833.8611 | 1065.3267 | 1922.3943 | Pa | 284.5644 | 668.8469 | 1216.4312 | 1672.0544 | 3269.7758
3600 W | 806 | 998 | 1288 | 1419 | 1665 |  | 3600 W | 886 | 1178 | 1558 | 1692 | 2030 |  | 3600 W | 981 | 1450 | 1738 | 2019 | 2373 | 3600 W | 1011 | 1653 | 2191 | 2662 | 3281
Pa | 117.8252 | 172.1068 | 2542.7139 | 3023.8277 | 780.8789 |  | Pa | 139.3545 | 230.9436 | 3574.0955 | 4142.6035 | 1101.2101 |  | Pa | 311.9969 | 614.397 | 813.8614 | 1031.027 | 1966.9559 | Pa | 328.7289 | 771.1445 | 1173.0208 | 1595.0241 | 3303.556
Water flow rate, L/h
FMS 90 | [6 empty] | FMS 110 | [6 empty] | FMS 140 | [5 empty] | FMS 190
Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  |  | Length |  |  | Width B, mm |  |  | Length |  |  | Width B, mm
Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 |  | Lc, mm | 200 | 250 | 300 | 340 | 420 | Lc, mm | 200 | 250 | 300 | 340 | 420
700 | 9.6612 | 12.0326 | 15.458 | 17.0389 | 20.0251 |  | 700 | 10.6274 | 14.1405 | 18.7077 | 20.3764 | 24.4166 |  | 700 | 11.7691 | 17.478 | 20.9034 | 24.2409 | 28.5446 | 700 | 12.1205 | 19.8494 | 26.3488 | 31.9699 | 39.4354
800 | 11.7691 | 14.5797 | 18.8833 | 20.8156 | 24.3287 |  | 800 | 12.9987 | 17.2146 | 22.8356 | 24.7679 | 29.6863 |  | 800 | 14.3162 | 21.2547 | 25.4705 | 29.5985 | 34.6926 | 800 | 14.8432 | 24.1531 | 32.0577 | 38.9962 | 48.0427
900 | 13.877 | 17.2146 | 22.2208 | 24.5044 | 28.7202 |  | 900 | 15.2823 | 20.2886 | 26.8758 | 29.1594 | 35.0439 |  | 900 | 16.9511 | 25.0314 | 29.9498 | 34.8683 | 40.9285 | 900 | 17.478 | 28.5446 | 37.7666 | 45.9348 | 56.65
1000 | 15.9849 | 19.8494 | 25.5584 | 28.1932 | 33.1117 |  | 1000 | 17.5659 | 23.3626 | 31.0038 | 33.6387 | 40.3137 |  | 1000 | 19.4981 | 28.808 | 34.5169 | 40.138 | 47.1644 | 1000 | 20.1129 | 32.8482 | 43.5634 | 52.8733 | 65.1694
1100 | 18.0929 | 22.3965 | 28.9837 | 31.8821 | 37.4153 |  | 1100 | 19.9373 | 26.4366 | 35.0439 | 38.0301 | 45.6713 |  | 1100 | 22.0452 | 32.5847 | 39.0841 | 45.4078 | 53.3124 | 1100 | 22.7478 | 37.1518 | 49.2723 | 59.8118 | 73.7767
1200 | 20.2008 | 25.0314 | 32.3212 | 35.6587 | 41.8068 |  | 1200 | 22.2208 | 29.5107 | 39.0841 | 42.4216 | 50.941 |  | 1200 | 24.5922 | 36.3614 | 43.5634 | 50.6776 | 59.5483 | 1200 | 25.3827 | 41.4555 | 54.9812 | 66.8382 | 82.2961
1300 | 22.3087 | 27.6663 | 35.6587 | 39.3476 | 46.1104 |  | 1300 | 24.5922 | 32.6725 | 43.2121 | 46.9009 | 56.2108 |  | 1300 | 27.1393 | 40.2259 | 48.1305 | 55.9473 | 65.6964 | 1300 | 28.0176 | 45.7591 | 60.6901 | 73.7767 | 90.9034
1400 | 24.4166 | 30.2133 | 39.0841 | 43.0364 | 50.5019 |  | 1400 | 26.8758 | 35.7466 | 47.2522 | 51.2924 | 61.5684 |  | 1400 | 29.7742 | 44.0025 | 52.6976 | 61.2171 | 71.9323 | 1400 | 30.6525 | 50.1506 | 66.399 | 80.7152 | 99.5107
1500 | 26.5245 | 32.8482 | 42.4216 | 46.7252 | 54.8055 |  | 1500 | 29.1594 | 38.8206 | 51.2924 | 55.7717 | 66.8382 |  | 1500 | 32.3212 | 47.7792 | 57.2648 | 66.4868 | 78.1682 | 1500 | 33.2873 | 54.4542 | 72.1958 | 87.6537 | 108.0301
1600 | 28.6324 | 35.4831 | 45.7591 | 50.5019 | 59.197 |  | 1600 | 31.5308 | 41.8946 | 55.4203 | 60.1631 | 72.1958 |  | 1600 | 34.8683 | 51.5559 | 61.7441 | 71.7566 | 84.3162 | 1600 | 35.9222 | 58.7579 | 77.9047 | 94.6801 | 116.6374
1800 | 32.8482 | 40.665 | 52.522 | 57.8796 | 67.8921 |  | 1800 | 36.0979 | 48.0427 | 63.5885 | 69.0339 | 82.7353 |  | 1800 | 39.9624 | 59.1092 | 70.8783 | 82.384 | 96.788 | 1800 | 41.2798 | 67.3651 | 89.3225 | 108.5571 | 133.7642
2000 | 37.064 | 45.9348 | 59.2848 | 65.3451 | 76.5872 |  | 2000 | 40.7528 | 54.1907 | 71.6688 | 77.8168 | 93.3626 |  | 2000 | 45.1443 | 66.7503 | 79.9247 | 92.9235 | 109.1719 | 2000 | 46.5496 | 76.0602 | 100.8281 | 122.522 | 150.9787
2200 | 41.2798 | 51.1167 | 65.9599 | 72.7227 | 85.2823 |  | 2200 | 45.4078 | 60.3388 | 79.8369 | 86.6876 | 103.99 |  | 2200 | 50.2384 | 74.3037 | 89.059 | 103.463 | 121.5559 | 2200 | 51.8193 | 84.6675 | 112.246 | 136.399 | 168.1054
2400 | 45.4956 | 56.2986 | 72.7227 | 80.1004 | 93.9774 |  | 2400 | 50.0628 | 66.4868 | 88.005 | 95.5584 | 114.6174 |  | 2400 | 55.3325 | 81.857 | 98.1054 | 114.0025 | 133.9398 | 2400 | 57.0891 | 93.2748 | 123.6638 | 150.2761 | 185.2322
2500 | 47.6035 | 58.9335 | 76.0602 | 83.8771 | 98.3689 |  | 2500 | 52.3463 | 69.5609 | 92.0452 | 99.9498 | 119.8871 |  | 2500 | 57.9674 | 85.6337 | 102.6726 | 119.2723 | 140.1757 | 2500 | 59.724 | 97.6663 | 129.4605 | 157.3024 | 193.8395
2600 | 49.7114 | 61.5684 | 79.4856 | 87.5659 | 102.6726 |  | 2600 | 54.7177 | 72.6349 | 96.1732 | 104.3413 | 125.2447 |  | 2600 | 60.5144 | 89.4981 | 107.1519 | 124.5421 | 146.3238 | 2600 | 62.3589 | 101.9699 | 135.1694 | 164.241 | 202.4467
2700 | 51.8193 | 64.1155 | 82.8231 | 91.2547 | 107.064 |  | 2700 | 57.0013 | 75.7089 | 100.2133 | 108.8206 | 130.5145 |  | 2700 | 63.0615 | 93.2748 | 111.719 | 129.8997 | 152.5596 | 2700 | 65.0816 | 106.2736 | 140.8783 | 171.1795 | 210.9662
2800 | 53.9272 | 66.7503 | 86.1606 | 94.9436 | 111.3677 |  | 2800 | 59.2848 | 78.783 | 104.2535 | 113.2121 | 135.7842 |  | 2800 | 65.6086 | 97.0515 | 116.2861 | 135.1694 | 158.7955 | 2800 | 67.7165 | 110.5772 | 146.5872 | 178.118 | 219.5735
2900 | 56.0351 | 69.3852 | 89.4981 | 98.7202 | 115.7591 |  | 2900 | 61.6562 | 81.857 | 108.3815 | 117.6914 | 141.1418 |  | 2900 | 68.1556 | 100.8281 | 120.8532 | 140.4392 | 164.9436 | 2900 | 70.3513 | 114.8808 | 152.2962 | 185.1443 | 228.1807
3000 | 58.1431 | 72.0201 | 92.9235 | 102.4091 | 120.0628 |  | 3000 | 63.9398 | 84.931 | 112.4216 | 122.0828 | 146.4116 |  | 3000 | 70.7027 | 104.6048 | 125.3325 | 145.709 | 171.1795 | 3000 | 72.9862 | 119.1845 | 158.0929 | 192.0829 | 236.7002
3200 | 62.3589 | 77.202 | 99.5985 | 109.7867 | 128.7579 |  | 3200 | 68.5948 | 91.1669 | 120.5897 | 130.9536 | 157.0389 |  | 3200 | 75.8846 | 112.246 | 134.4668 | 156.2485 | 183.5634 | 3200 | 78.256 | 127.8796 | 169.5107 | 205.9599 | 253.9148
3400 | 66.5747 | 82.384 | 106.3614 | 117.2522 | 137.453 |  | 3400 | 73.2497 | 97.315 | 128.7579 | 139.7366 | 167.6663 |  | 3400 | 80.9787 | 119.7993 | 143.5132 | 166.788 | 195.9474 | 3400 | 83.5257 | 136.4869 | 180.9285 | 219.9248 | 271.0415
3600 | 70.7905 | 87.6537 | 113.1243 | 124.6299 | 146.2359 |  | 3600 | 77.8168 | 103.463 | 136.8382 | 148.6073 | 178.2937 |  | 3600 | 86.1606 | 127.3526 | 152.6475 | 177.3275 | 208.4191 | 3600 | 88.7955 | 145.182 | 192.4342 | 233.8018 | 288.1682

## F1S Heating
AQUILO F1S -Heating only | [17 empty] | 070721 MII
Re corrected heat outputs
Re corrected flow resistances
ΔT according to DIN 4703-3: |  |  |  | Tflow = | 75 | oC |  | Fan speed = | 2 | Select 1, 2 or 3
|  |  |  | Trtn = | 65 | oC |  | Design recommendation, fan speed 2
|  |  |  | Tin = | 20 | oC
|  |  |  | ΔTar = | 50 | K |  |  |  | High flow resistance
Standard heat outputs at ΔT50K
F1S 75-170 |  |  |  | F1S 75-200 |  |  |  |  | F1S 75-230 |  |  |  |  | F1S 110-230 |  |  |  |  | F1S 110-250
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
700 | 192 | 342 | 427 | 700 | 285 | 506 | 633 |  | 700 | 313 | 556 | 695 |  | 700 | 397 | 706 | 882 |  | 700 | 541 | 962 | 1202 | Error
800 | 192 | 342 | 427 | 800 | 285 | 506 | 633 |  | 800 | 313 | 556 | 695 |  | 800 | 397 | 706 | 882 |  | 800 | 541 | 962 | 1202 | Error
900 | 192 | 342 | 427 | 900 | 285 | 506 | 633 |  | 900 | 313 | 556 | 695 |  | 900 | 397 | 706 | 882 |  | 900 | 541 | 962 | 1202 | Error
1000 | 397 | 706 | 883 | 1000 | 588 | 1046 | 1307 |  | 1000 | 645 | 1147 | 1434 |  | 1000 | 820 | 1458 | 1822 |  | 1000 | 1117 | 1986 | 2482 | Error
1100 | 397 | 706 | 883 | 1100 | 588 | 1046 | 1307 |  | 1100 | 645 | 1147 | 1434 |  | 1100 | 820 | 1458 | 1822 |  | 1100 | 1117 | 1986 | 2482 | Error
1200 | 397 | 706 | 883 | 1200 | 588 | 1046 | 1307 |  | 1200 | 645 | 1147 | 1434 |  | 1200 | 820 | 1458 | 1822 |  | 1200 | 1117 | 1986 | 2482 | Error
1300 | 602 | 1070 | 1338 | 1300 | 891 | 1585 | 1981 |  | 1300 | 978 | 1739 | 2174 |  | 1300 | 1242 | 2209 | 2761 |  | 1300 | 1693 | 3010 | 3763 | Error
1400 | 602 | 1070 | 1338 | 1400 | 891 | 1585 | 1981 |  | 1400 | 978 | 1739 | 2174 |  | 1400 | 1242 | 2209 | 2761 |  | 1400 | 1693 | 3010 | 3763 | Error
1500 | 714 | 1269 | 1586 | 1500 | 1057 | 1878 | 2348 |  | 1500 | 1160 | 2062 | 2578 |  | 1500 | 1473 | 2619 | 3274 |  | 1500 | 2007 | 3569 | 4461 | Error
1600 | 714 | 1269 | 1586 | 1600 | 1057 | 1878 | 2348 |  | 1600 | 1160 | 2062 | 2578 |  | 1600 | 1473 | 2619 | 3274 |  | 1600 | 2007 | 3569 | 4461 | Error
1800 | 875 | 1555 | 1944 | 1800 | 1296 | 2303 | 2879 |  | 1800 | 1422 | 2528 | 3160 |  | 1800 | 1806 | 3211 | 4014 |  | 1800 | 2461 | 4375 | 5469 | Error
2000 | 987 | 1754 | 2193 | 2000 | 1461 | 2598 | 3247 |  | 2000 | 1604 | 2851 | 3564 |  | 2000 | 2037 | 3621 | 4526 |  | 2000 | 2775 | 4934 | 6167 | Error
2200 | 1086 | 1930 | 2413 | 2200 | 1608 | 2859 | 3574 |  | 2200 | 1765 | 3138 | 3922 |  | 2200 | 2242 | 3986 | 4982 |  | 2200 | 3055 | 5430 | 6788 | Error
2400 | 1197 | 2129 | 2661 | 2400 | 1773 | 3153 | 3941 |  | 2400 | 1947 | 3461 | 4326 |  | 2400 | 2472 | 4395 | 5494 |  | 2400 | 3369 | 5989 | 7486 | Error
2500 | 1297 | 2306 | 2882 | 2500 | 1921 | 3414 | 4268 |  | 2500 | 2108 | 3747 | 4684 |  | 2500 | 2678 | 4760 | 5950 |  | 2500 | 3648 | 6486 | 8107 | Error
2600 | 1409 | 2504 | 3130 | 2600 | 2086 | 3708 | 4635 |  | 2600 | 2290 | 4070 | 5088 |  | 2600 | 2908 | 5170 | 6462 |  | 2600 | 3962 | 7044 | 8805 | Error
2800 | 1564 | 2780 | 3475 | 2800 | 2316 | 4117 | 5146 |  | 2800 | 2542 | 4518 | 5648 |  | 2800 | 3228 | 5739 | 7174 |  | 2800 | 4399 | 7820 | 9775 | Error
3000 | 1564 | 2780 | 3475 | 3000 | 2316 | 4117 | 5146 |  | 3000 | 2542 | 4518 | 5648 |  | 3000 | 3228 | 5739 | 7174 |  | 3000 | 4399 | 7820 | 9775 | Error
Reynolds numbers at standard output conditions 75/65/20
F1S 75-170 |  |  |  | F1S 75-200 |  |  |  |  | F1S 75-230 |  |  |  |  | F1S 110-230 |  |  |  |  | F1S 110-250
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
700 | 768.0594 | 1368.1058 | 1708.1321 | 700 | 1140.0882 | 2024.1566 | 2532.1959 |  | 700 | 1252.0969 | 2224.1721 | 2780.2151 |  | 700 | 1588.1229 | 2824.2185 | 3528.2729 |  | 700 | 2164.1674 | 3848.2977 | 4808.372
800 | 768.0594 | 1368.1058 | 1708.1321 | 800 | 1140.0882 | 2024.1566 | 2532.1959 |  | 800 | 1252.0969 | 2224.1721 | 2780.2151 |  | 800 | 1588.1229 | 2824.2185 | 3528.2729 |  | 800 | 2164.1674 | 3848.2977 | 4808.372
900 | 768.0594 | 1368.1058 | 1708.1321 | 900 | 1140.0882 | 2024.1566 | 2532.1959 |  | 900 | 1252.0969 | 2224.1721 | 2780.2151 |  | 900 | 1588.1229 | 2824.2185 | 3528.2729 |  | 900 | 2164.1674 | 3848.2977 | 4808.372
1000 | 1588.1229 | 2824.2185 | 3532.2733 | 1000 | 2352.182 | 4184.3237 | 5228.4045 |  | 1000 | 2580.1996 | 4588.355 | 5736.4438 |  | 1000 | 3280.2538 | 5832.4512 | 7288.5638 |  | 1000 | 4468.3457 | 7944.6146 | 9928.7681
1100 | 1588.1229 | 2824.2185 | 3532.2733 | 1100 | 2352.182 | 4184.3237 | 5228.4045 |  | 1100 | 2580.1996 | 4588.355 | 5736.4438 |  | 1100 | 3280.2538 | 5832.4512 | 7288.5638 |  | 1100 | 4468.3457 | 7944.6146 | 9928.7681
1200 | 1588.1229 | 2824.2185 | 3532.2733 | 1200 | 2352.182 | 4184.3237 | 5228.4045 |  | 1200 | 2580.1996 | 4588.355 | 5736.4438 |  | 1200 | 3280.2538 | 5832.4512 | 7288.5638 |  | 1200 | 4468.3457 | 7944.6146 | 9928.7681
1300 | 2408.1863 | 4280.3311 | 5352.4141 | 1300 | 3564.2757 | 6340.4905 | 7924.613 |  | 1300 | 3912.3027 | 6956.5382 | 8696.6728 |  | 1300 | 4968.3844 | 8836.6836 | 11044.8544 |  | 1300 | 6772.5239 | 12040.9315 | 15053.1645
1400 | 2408.1863 | 4280.3311 | 5352.4141 | 1400 | 3564.2757 | 6340.4905 | 7924.613 |  | 1400 | 3912.3027 | 6956.5382 | 8696.6728 |  | 1400 | 4968.3844 | 8836.6836 | 11044.8544 |  | 1400 | 6772.5239 | 12040.9315 | 15053.1645
1500 | 2856.221 | 5076.3927 | 6344.4908 | 1500 | 4228.3271 | 7512.5812 | 9392.7266 |  | 1500 | 4640.359 | 8248.6381 | 10312.7978 |  | 1500 | 5892.4558 | 10476.8105 | 13097.0132 |  | 1500 | 8028.6211 | 14277.1045 | 17845.3805
1600 | 2856.221 | 5076.3927 | 6344.4908 | 1600 | 4228.3271 | 7512.5812 | 9392.7266 |  | 1600 | 4640.359 | 8248.6381 | 10312.7978 |  | 1600 | 5892.4558 | 10476.8105 | 13097.0132 |  | 1600 | 8028.6211 | 14277.1045 | 17845.3805
1800 | 3500.2708 | 6220.4812 | 7776.6016 | 1800 | 5184.4011 | 9212.7127 | 11516.8909 |  | 1800 | 5688.4401 | 10112.7823 | 12640.9779 |  | 1800 | 7224.5589 | 12844.9937 | 16057.2422 |  | 1800 | 9844.7616 | 17501.3539 | 21877.6925
2000 | 3948.3054 | 7016.5428 | 8772.6787 | 2000 | 5844.4521 | 10392.804 | 12989.0048 |  | 2000 | 6416.4964 | 11404.8823 | 14257.1029 |  | 2000 | 8148.6304 | 14485.1206 | 18105.4006 |  | 2000 | 11100.8588 | 19737.5269 | 24669.9085
2200 | 4344.3361 | 7720.5973 | 9652.7467 | 2200 | 6432.4976 | 11436.8848 | 14297.106 |  | 2200 | 7060.5462 | 12552.9711 | 15689.2137 |  | 2200 | 8968.6938 | 15945.2335 | 19929.5417 |  | 2200 | 12220.9454 | 21721.6804 | 27154.1006
2400 | 4788.3704 | 8516.6588 | 10644.8235 | 2400 | 7092.5487 | 12612.9757 | 15765.2196 |  | 2400 | 7788.6025 | 13845.0711 | 17305.3387 |  | 2400 | 9888.765 | 17581.3601 | 21977.7002 |  | 2400 | 13477.0426 | 23957.8534 | 29946.3166
2500 | 5188.4014 | 9224.7136 | 11528.8919 | 2500 | 7684.5945 | 13657.0565 | 17073.3208 |  | 2500 | 8432.6523 | 14989.1596 | 18737.4495 |  | 2500 | 10712.8287 | 19041.473 | 23801.8413 |  | 2500 | 14593.1289 | 25946.0072 | 32430.5088
2600 | 5636.436 | 10016.7749 | 12520.9686 | 2600 | 8344.6455 | 14833.1475 | 18541.4344 |  | 2600 | 9160.7087 | 16281.2595 | 20353.5746 |  | 2600 | 11632.8999 | 20681.5999 | 25849.9998 |  | 2600 | 15849.2261 | 28178.1799 | 35222.7248
2800 | 6256.484 | 11120.8603 | 13901.0754 | 2800 | 9264.7167 | 16469.2741 | 20585.5925 |  | 2800 | 10168.7867 | 18073.3982 | 22593.7479 |  | 2800 | 12912.9989 | 22957.776 | 28698.2201 |  | 2800 | 17597.3613 | 31282.42 | 39103.025
3000 | 6256.484 | 11120.8603 | 13901.0754 | 3000 | 9264.7167 | 16469.2741 | 20585.5925 |  | 3000 | 10168.7867 | 18073.3982 | 22593.7479 |  | 3000 | 12912.9989 | 22957.776 | 28698.2201 |  | 3000 | 17597.3613 | 31282.42 | 39103.025
Heat outputs at calculation conditions without correction
F1S 75-170 |  |  |  | F1S 75-200 |  |  |  |  | F1S 75-230 |  |  |  |  | F1S 110-230 |  |  |  |  | F1S 110-250
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
700 | 192 | 342 | 427 | 700 | 285 | 506 | 633 |  | 700 | 313 | 556 | 695 |  | 700 | 397 | 706 | 882 |  | 700 | 541 | 962 | 1202
700 | 192 | 342 | 427 | 800 | 285 | 506 | 633 |  | 800 | 313 | 556 | 695 |  | 800 | 397 | 706 | 882 |  | 800 | 541 | 962 | 1202
700 | 192 | 342 | 427 | 900 | 285 | 506 | 633 |  | 900 | 313 | 556 | 695 |  | 900 | 397 | 706 | 882 |  | 900 | 541 | 962 | 1202
1000 | 397 | 706 | 883 | 1000 | 588 | 1046 | 1307 |  | 1000 | 645 | 1147 | 1434 |  | 1000 | 820 | 1458 | 1822 |  | 1000 | 1117 | 1986 | 2482
1000 | 397 | 706 | 883 | 1100 | 588 | 1046 | 1307 |  | 1100 | 645 | 1147 | 1434 |  | 1100 | 820 | 1458 | 1822 |  | 1100 | 1117 | 1986 | 2482
1000 | 397 | 706 | 883 | 1200 | 588 | 1046 | 1307 |  | 1200 | 645 | 1147 | 1434 |  | 1200 | 820 | 1458 | 1822 |  | 1200 | 1117 | 1986 | 2482
1300 | 602 | 1070 | 1338 | 1300 | 891 | 1585 | 1981 |  | 1300 | 978 | 1739 | 2174 |  | 1300 | 1242 | 2209 | 2761 |  | 1300 | 1693 | 3010 | 3763
1300 | 602 | 1070 | 1338 | 1400 | 891 | 1585 | 1981 |  | 1400 | 978 | 1739 | 2174 |  | 1400 | 1242 | 2209 | 2761 |  | 1400 | 1693 | 3010 | 3763
1500 | 714 | 1269 | 1586 | 1500 | 1057 | 1878 | 2348 |  | 1500 | 1160 | 2062 | 2578 |  | 1500 | 1473 | 2619 | 3274 |  | 1500 | 2007 | 3569 | 4461
1500 | 714 | 1269 | 1586 | 1600 | 1057 | 1878 | 2348 |  | 1600 | 1160 | 2062 | 2578 |  | 1600 | 1473 | 2619 | 3274 |  | 1600 | 2007 | 3569 | 4461
1800 | 875 | 1555 | 1944 | 1800 | 1296 | 2303 | 2879 |  | 1800 | 1422 | 2528 | 3160 |  | 1800 | 1806 | 3211 | 4014 |  | 1800 | 2461 | 4375 | 5469
2000 | 987 | 1754 | 2193 | 2000 | 1461 | 2598 | 3247 |  | 2000 | 1604 | 2851 | 3564 |  | 2000 | 2037 | 3621 | 4526 |  | 2000 | 2775 | 4934 | 6167
2200 | 1086 | 1930 | 2413 | 2200 | 1608 | 2859 | 3574 |  | 2200 | 1765 | 3138 | 3922 |  | 2200 | 2242 | 3986 | 4982 |  | 2200 | 3055 | 5430 | 6788
2400 | 1197 | 2129 | 2661 | 2400 | 1773 | 3153 | 3941 |  | 2400 | 1947 | 3461 | 4326 |  | 2400 | 2472 | 4395 | 5494 |  | 2400 | 3369 | 5989 | 7486
2500 | 1297 | 2306 | 2882 | 2500 | 1921 | 3414 | 4268 |  | 2500 | 2108 | 3747 | 4684 |  | 2500 | 2678 | 4760 | 5950 |  | 2500 | 3648 | 6486 | 8107
2600 | 1409 | 2504 | 3130 | 2600 | 2086 | 3708 | 4635 |  | 2600 | 2290 | 4070 | 5088 |  | 2600 | 2908 | 5170 | 6462 |  | 2600 | 3962 | 7044 | 8805
2800 | 1564 | 2780 | 3475 | 2800 | 2316 | 4117 | 5146 |  | 2800 | 2542 | 4518 | 5648 |  | 2800 | 3228 | 5739 | 7174 |  | 2800 | 4399 | 7820 | 9775
2800 | 1564 | 2780 | 3475 | 3000 | 2316 | 4117 | 5146 |  | 3000 | 2542 | 4518 | 5648 |  | 3000 | 3228 | 5739 | 7174 |  | 3000 | 4399 | 7820 | 9775
Reynolds numbers at Twater=70 and (Tflow-Trtn) according to calculation values
F1S 75-170 |  |  |  | F1S 75-200 |  |  |  |  | F1S 75-230 |  |  |  |  | F1S 110-230 |  |  |  |  | F1S 110-250
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
700 | 768.0594 | 1368.1058 | 1708.1321 | 700 | 1140.0882 | 2024.1566 | 2532.1959 |  | 700 | 1252.0969 | 2224.1721 | 2780.2151 |  | 700 | 1588.1229 | 2824.2185 | 3528.2729 |  | 700 | 2164.1674 | 3848.2977 | 4808.372
800 | 768.0594 | 1368.1058 | 1708.1321 | 800 | 1140.0882 | 2024.1566 | 2532.1959 |  | 800 | 1252.0969 | 2224.1721 | 2780.2151 |  | 800 | 1588.1229 | 2824.2185 | 3528.2729 |  | 800 | 2164.1674 | 3848.2977 | 4808.372
900 | 768.0594 | 1368.1058 | 1708.1321 | 900 | 1140.0882 | 2024.1566 | 2532.1959 |  | 900 | 1252.0969 | 2224.1721 | 2780.2151 |  | 900 | 1588.1229 | 2824.2185 | 3528.2729 |  | 900 | 2164.1674 | 3848.2977 | 4808.372
1000 | 1588.1229 | 2824.2185 | 3532.2733 | 1000 | 2352.182 | 4184.3237 | 5228.4045 |  | 1000 | 2580.1996 | 4588.355 | 5736.4438 |  | 1000 | 3280.2538 | 5832.4512 | 7288.5638 |  | 1000 | 4468.3457 | 7944.6146 | 9928.7681
1100 | 1588.1229 | 2824.2185 | 3532.2733 | 1100 | 2352.182 | 4184.3237 | 5228.4045 |  | 1100 | 2580.1996 | 4588.355 | 5736.4438 |  | 1100 | 3280.2538 | 5832.4512 | 7288.5638 |  | 1100 | 4468.3457 | 7944.6146 | 9928.7681
1200 | 1588.1229 | 2824.2185 | 3532.2733 | 1200 | 2352.182 | 4184.3237 | 5228.4045 |  | 1200 | 2580.1996 | 4588.355 | 5736.4438 |  | 1200 | 3280.2538 | 5832.4512 | 7288.5638 |  | 1200 | 4468.3457 | 7944.6146 | 9928.7681
1300 | 2408.1863 | 4280.3311 | 5352.4141 | 1300 | 3564.2757 | 6340.4905 | 7924.613 |  | 1300 | 3912.3027 | 6956.5382 | 8696.6728 |  | 1300 | 4968.3844 | 8836.6836 | 11044.8544 |  | 1300 | 6772.5239 | 12040.9315 | 15053.1645
1400 | 2408.1863 | 4280.3311 | 5352.4141 | 1400 | 3564.2757 | 6340.4905 | 7924.613 |  | 1400 | 3912.3027 | 6956.5382 | 8696.6728 |  | 1400 | 4968.3844 | 8836.6836 | 11044.8544 |  | 1400 | 6772.5239 | 12040.9315 | 15053.1645
1500 | 2856.221 | 5076.3927 | 6344.4908 | 1500 | 4228.3271 | 7512.5812 | 9392.7266 |  | 1500 | 4640.359 | 8248.6381 | 10312.7978 |  | 1500 | 5892.4558 | 10476.8105 | 13097.0132 |  | 1500 | 8028.6211 | 14277.1045 | 17845.3805
1600 | 2856.221 | 5076.3927 | 6344.4908 | 1600 | 4228.3271 | 7512.5812 | 9392.7266 |  | 1600 | 4640.359 | 8248.6381 | 10312.7978 |  | 1600 | 5892.4558 | 10476.8105 | 13097.0132 |  | 1600 | 8028.6211 | 14277.1045 | 17845.3805
1800 | 3500.2708 | 6220.4812 | 7776.6016 | 1800 | 5184.4011 | 9212.7127 | 11516.8909 |  | 1800 | 5688.4401 | 10112.7823 | 12640.9779 |  | 1800 | 7224.5589 | 12844.9937 | 16057.2422 |  | 1800 | 9844.7616 | 17501.3539 | 21877.6925
2000 | 3948.3054 | 7016.5428 | 8772.6787 | 2000 | 5844.4521 | 10392.804 | 12989.0048 |  | 2000 | 6416.4964 | 11404.8823 | 14257.1029 |  | 2000 | 8148.6304 | 14485.1206 | 18105.4006 |  | 2000 | 11100.8588 | 19737.5269 | 24669.9085
2200 | 4344.3361 | 7720.5973 | 9652.7467 | 2200 | 6432.4976 | 11436.8848 | 14297.106 |  | 2200 | 7060.5462 | 12552.9711 | 15689.2137 |  | 2200 | 8968.6938 | 15945.2335 | 19929.5417 |  | 2200 | 12220.9454 | 21721.6804 | 27154.1006
2400 | 4788.3704 | 8516.6588 | 10644.8235 | 2400 | 7092.5487 | 12612.9757 | 15765.2196 |  | 2400 | 7788.6025 | 13845.0711 | 17305.3387 |  | 2400 | 9888.765 | 17581.3601 | 21977.7002 |  | 2400 | 13477.0426 | 23957.8534 | 29946.3166
2500 | 5188.4014 | 9224.7136 | 11528.8919 | 2500 | 7684.5945 | 13657.0565 | 17073.3208 |  | 2500 | 8432.6523 | 14989.1596 | 18737.4495 |  | 2500 | 10712.8287 | 19041.473 | 23801.8413 |  | 2500 | 14593.1289 | 25946.0072 | 32430.5088
2600 | 5636.436 | 10016.7749 | 12520.9686 | 2600 | 8344.6455 | 14833.1475 | 18541.4344 |  | 2600 | 9160.7087 | 16281.2595 | 20353.5746 |  | 2600 | 11632.8999 | 20681.5999 | 25849.9998 |  | 2600 | 15849.2261 | 28178.1799 | 35222.7248
2800 | 6256.484 | 11120.8603 | 13901.0754 | 2800 | 9264.7167 | 16469.2741 | 20585.5925 |  | 2800 | 10168.7867 | 18073.3982 | 22593.7479 |  | 2800 | 12912.9989 | 22957.776 | 28698.2201 |  | 2800 | 17597.3613 | 31282.42 | 39103.025
3000 | 6256.484 | 11120.8603 | 13901.0754 | 3000 | 9264.7167 | 16469.2741 | 20585.5925 |  | 3000 | 10168.7867 | 18073.3982 | 22593.7479 |  | 3000 | 12912.9989 | 22957.776 | 28698.2201 |  | 3000 | 17597.3613 | 31282.42 | 39103.025
Reynolds numbers at calculation conditions
F1S 75-170 |  |  |  | F1S 75-200 |  |  |  |  | F1S 75-230 |  |  |  |  | F1S 110-230 |  |  |  |  | F1S 110-250
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
700 | 768.0594 | 1368.1058 | 1708.1321 | 700 | 1140.0882 | 2024.1566 | 2532.1959 |  | 700 | 1252.0969 | 2224.1721 | 2780.2151 |  | 700 | 1588.1229 | 2824.2185 | 3528.2729 |  | 700 | 2164.1674 | 3848.2977 | 4808.372
800 | 768.0594 | 1368.1058 | 1708.1321 | 800 | 1140.0882 | 2024.1566 | 2532.1959 |  | 800 | 1252.0969 | 2224.1721 | 2780.2151 |  | 800 | 1588.1229 | 2824.2185 | 3528.2729 |  | 800 | 2164.1674 | 3848.2977 | 4808.372
900 | 768.0594 | 1368.1058 | 1708.1321 | 900 | 1140.0882 | 2024.1566 | 2532.1959 |  | 900 | 1252.0969 | 2224.1721 | 2780.2151 |  | 900 | 1588.1229 | 2824.2185 | 3528.2729 |  | 900 | 2164.1674 | 3848.2977 | 4808.372
1000 | 1588.1229 | 2824.2185 | 3532.2733 | 1000 | 2352.182 | 4184.3237 | 5228.4045 |  | 1000 | 2580.1996 | 4588.355 | 5736.4438 |  | 1000 | 3280.2538 | 5832.4512 | 7288.5638 |  | 1000 | 4468.3457 | 7944.6146 | 9928.7681
1100 | 1588.1229 | 2824.2185 | 3532.2733 | 1100 | 2352.182 | 4184.3237 | 5228.4045 |  | 1100 | 2580.1996 | 4588.355 | 5736.4438 |  | 1100 | 3280.2538 | 5832.4512 | 7288.5638 |  | 1100 | 4468.3457 | 7944.6146 | 9928.7681
1200 | 1588.1229 | 2824.2185 | 3532.2733 | 1200 | 2352.182 | 4184.3237 | 5228.4045 |  | 1200 | 2580.1996 | 4588.355 | 5736.4438 |  | 1200 | 3280.2538 | 5832.4512 | 7288.5638 |  | 1200 | 4468.3457 | 7944.6146 | 9928.7681
1300 | 2408.1863 | 4280.3311 | 5352.4141 | 1300 | 3564.2757 | 6340.4905 | 7924.613 |  | 1300 | 3912.3027 | 6956.5382 | 8696.6728 |  | 1300 | 4968.3844 | 8836.6836 | 11044.8544 |  | 1300 | 6772.5239 | 12040.9315 | 15053.1645
1400 | 2408.1863 | 4280.3311 | 5352.4141 | 1400 | 3564.2757 | 6340.4905 | 7924.613 |  | 1400 | 3912.3027 | 6956.5382 | 8696.6728 |  | 1400 | 4968.3844 | 8836.6836 | 11044.8544 |  | 1400 | 6772.5239 | 12040.9315 | 15053.1645
1500 | 2856.221 | 5076.3927 | 6344.4908 | 1500 | 4228.3271 | 7512.5812 | 9392.7266 |  | 1500 | 4640.359 | 8248.6381 | 10312.7978 |  | 1500 | 5892.4558 | 10476.8105 | 13097.0132 |  | 1500 | 8028.6211 | 14277.1045 | 17845.3805
1600 | 2856.221 | 5076.3927 | 6344.4908 | 1600 | 4228.3271 | 7512.5812 | 9392.7266 |  | 1600 | 4640.359 | 8248.6381 | 10312.7978 |  | 1600 | 5892.4558 | 10476.8105 | 13097.0132 |  | 1600 | 8028.6211 | 14277.1045 | 17845.3805
1800 | 3500.2708 | 6220.4812 | 7776.6016 | 1800 | 5184.4011 | 9212.7127 | 11516.8909 |  | 1800 | 5688.4401 | 10112.7823 | 12640.9779 |  | 1800 | 7224.5589 | 12844.9937 | 16057.2422 |  | 1800 | 9844.7616 | 17501.3539 | 21877.6925
2000 | 3948.3054 | 7016.5428 | 8772.6787 | 2000 | 5844.4521 | 10392.804 | 12989.0048 |  | 2000 | 6416.4964 | 11404.8823 | 14257.1029 |  | 2000 | 8148.6304 | 14485.1206 | 18105.4006 |  | 2000 | 11100.8588 | 19737.5269 | 24669.9085
2200 | 4344.3361 | 7720.5973 | 9652.7467 | 2200 | 6432.4976 | 11436.8848 | 14297.106 |  | 2200 | 7060.5462 | 12552.9711 | 15689.2137 |  | 2200 | 8968.6938 | 15945.2335 | 19929.5417 |  | 2200 | 12220.9454 | 21721.6804 | 27154.1006
2400 | 4788.3704 | 8516.6588 | 10644.8235 | 2400 | 7092.5487 | 12612.9757 | 15765.2196 |  | 2400 | 7788.6025 | 13845.0711 | 17305.3387 |  | 2400 | 9888.765 | 17581.3601 | 21977.7002 |  | 2400 | 13477.0426 | 23957.8534 | 29946.3166
2500 | 5188.4014 | 9224.7136 | 11528.8919 | 2500 | 7684.5945 | 13657.0565 | 17073.3208 |  | 2500 | 8432.6523 | 14989.1596 | 18737.4495 |  | 2500 | 10712.8287 | 19041.473 | 23801.8413 |  | 2500 | 14593.1289 | 25946.0072 | 32430.5088
2600 | 5636.436 | 10016.7749 | 12520.9686 | 2600 | 8344.6455 | 14833.1475 | 18541.4344 |  | 2600 | 9160.7087 | 16281.2595 | 20353.5746 |  | 2600 | 11632.8999 | 20681.5999 | 25849.9998 |  | 2600 | 15849.2261 | 28178.1799 | 35222.7248
2800 | 6256.484 | 11120.8603 | 13901.0754 | 2800 | 9264.7167 | 16469.2741 | 20585.5925 |  | 2800 | 10168.7867 | 18073.3982 | 22593.7479 |  | 2800 | 12912.9989 | 22957.776 | 28698.2201 |  | 2800 | 17597.3613 | 31282.42 | 39103.025
3000 | 6256.484 | 11120.8603 | 13901.0754 | 3000 | 9264.7167 | 16469.2741 | 20585.5925 |  | 3000 | 10168.7867 | 18073.3982 | 22593.7479 |  | 3000 | 12912.9989 | 22957.776 | 28698.2201 |  | 3000 | 17597.3613 | 31282.42 | 39103.025
Re corrected heat outputs - W
F1S 75-170 |  |  |  | F1S 75-200 |  |  |  |  | F1S 75-230 |  |  |  |  | F1S 110-230 |  |  |  |  | F1S 110-250
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
700 | 192 | 342 | 427 | 700 | 285 | 506 | 633 |  | 700 | 313 | 556 | 695 |  | 700 | 397 | 706 | 882 |  | 700 | 541 | 962 | 1202
800 | 192 | 342 | 427 | 800 | 285 | 506 | 633 |  | 800 | 313 | 556 | 695 |  | 800 | 397 | 706 | 882 |  | 800 | 541 | 962 | 1202
900 | 192 | 342 | 427 | 900 | 285 | 506 | 633 |  | 900 | 313 | 556 | 695 |  | 900 | 397 | 706 | 882 |  | 900 | 541 | 962 | 1202
1000 | 397 | 706 | 883 | 1000 | 588 | 1046 | 1307 |  | 1000 | 645 | 1147 | 1434 |  | 1000 | 820 | 1458 | 1822 |  | 1000 | 1117 | 1986 | 2482
1100 | 397 | 706 | 883 | 1100 | 588 | 1046 | 1307 |  | 1100 | 645 | 1147 | 1434 |  | 1100 | 820 | 1458 | 1822 |  | 1100 | 1117 | 1986 | 2482
1200 | 397 | 706 | 883 | 1200 | 588 | 1046 | 1307 |  | 1200 | 645 | 1147 | 1434 |  | 1200 | 820 | 1458 | 1822 |  | 1200 | 1117 | 1986 | 2482
1300 | 602 | 1070 | 1338 | 1300 | 891 | 1585 | 1981 |  | 1300 | 978 | 1739 | 2174 |  | 1300 | 1242 | 2209 | 2761 |  | 1300 | 1693 | 3010 | 3763
1400 | 602 | 1070 | 1338 | 1400 | 891 | 1585 | 1981 |  | 1400 | 978 | 1739 | 2174 |  | 1400 | 1242 | 2209 | 2761 |  | 1400 | 1693 | 3010 | 3763
1500 | 714 | 1269 | 1586 | 1500 | 1057 | 1878 | 2348 |  | 1500 | 1160 | 2062 | 2578 |  | 1500 | 1473 | 2619 | 3274 |  | 1500 | 2007 | 3569 | 4461
1600 | 714 | 1269 | 1586 | 1600 | 1057 | 1878 | 2348 |  | 1600 | 1160 | 2062 | 2578 |  | 1600 | 1473 | 2619 | 3274 |  | 1600 | 2007 | 3569 | 4461
1800 | 875 | 1555 | 1944 | 1800 | 1296 | 2303 | 2879 |  | 1800 | 1422 | 2528 | 3160 |  | 1800 | 1806 | 3211 | 4014 |  | 1800 | 2461 | 4375 | 5469
2000 | 987 | 1754 | 2193 | 2000 | 1461 | 2598 | 3247 |  | 2000 | 1604 | 2851 | 3564 |  | 2000 | 2037 | 3621 | 4526 |  | 2000 | 2775 | 4934 | 6167
2200 | 1086 | 1930 | 2413 | 2200 | 1608 | 2859 | 3574 |  | 2200 | 1765 | 3138 | 3922 |  | 2200 | 2242 | 3986 | 4982 |  | 2200 | 3055 | 5430 | 6788
2400 | 1197 | 2129 | 2661 | 2400 | 1773 | 3153 | 3941 |  | 2400 | 1947 | 3461 | 4326 |  | 2400 | 2472 | 4395 | 5494 |  | 2400 | 3369 | 5989 | 7486
2500 | 1297 | 2306 | 2882 | 2500 | 1921 | 3414 | 4268 |  | 2500 | 2108 | 3747 | 4684 |  | 2500 | 2678 | 4760 | 5950 |  | 2500 | 3648 | 6486 | 8107
2600 | 1409 | 2504 | 3130 | 2600 | 2086 | 3708 | 4635 |  | 2600 | 2290 | 4070 | 5088 |  | 2600 | 2908 | 5170 | 6462 |  | 2600 | 3962 | 7044 | 8805
2800 | 1564 | 2780 | 3475 | 2800 | 2316 | 4117 | 5146 |  | 2800 | 2542 | 4518 | 5648 |  | 2800 | 3228 | 5739 | 7174 |  | 2800 | 4399 | 7820 | 9775
3000 | 1564 | 2780 | 3475 | 3000 | 2316 | 4117 | 5146 |  | 3000 | 2542 | 4518 | 5648 |  | 3000 | 3228 | 5739 | 7174 |  | 3000 | 4399 | 7820 | 9775
Flow resistance / Pressure drop - Pa
F1S 75-170 |  |  |  | F1S 75-200 |  |  |  |  | F1S 75-230 |  |  |  |  | F1S 110-230 |  |  |  |  | F1S 110-250
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
700 | 18.5047 | 54.1454 | 81.8166 | 700 | 67.1876 | 189.8799 | 284.765 |  | 700 | 21.9746 | 69.0023 | 107.6119 |  | 700 | 122.4052 | 346.9543 | 519.055 |  | 700 | 65.3445 | 205.609 | 320.3905
800 | 22.9154 | 66.9026 | 101.0074 | 800 | 88.4477 | 249.6975 | 374.3185 |  | 800 | 27.679 | 86.9943 | 135.7196 |  | 800 | 161.0388 | 455.9729 | 681.8687 |  | 800 | 82.3792 | 259.4475 | 404.4279
900 | 27.2288 | 79.3196 | 119.6521 | 900 | 108.9533 | 307.2642 | 460.4275 |  | 900 | 33.3329 | 104.8546 | 163.638 |  | 900 | 198.2535 | 560.7539 | 838.2185 |  | 900 | 99.2879 | 312.9697 | 488.0214
1000 | 120.4086 | 348.9263 | 527.5911 | 1000 | 475.5094 | 1344.3509 | 2009.4058 |  | 1000 | 164.8378 | 520.0729 | 812.1715 |  | 1000 | 866.4948 | 2447.5936 | 3659.1401 |  | 1000 | 493.2758 | 1555.7587 | 2427.7279
1100 | 135.8178 | 392.7108 | 593.2851 | 1100 | 545.1619 | 1539.6943 | 2300.4754 |  | 1100 | 188.4443 | 594.9983 | 929.4487 |  | 1100 | 992.8318 | 2801.592 | 4186.7075 |  | 1100 | 564.3211 | 1781.164 | 2780.2743
1200 | 150.7874 | 435.032 | 656.6574 | 1200 | 612.0409 | 1726.8373 | 2579.0819 |  | 1200 | 211.7835 | 669.1531 | 1045.567 |  | 1200 | 1113.9808 | 3140.2865 | 4691.0225 |  | 1200 | 634.6324 | 2004.4743 | 3129.6856
1300 | 355.1612 | 1021.421 | 1539.911 | 1300 | 1428.2808 | 4025.7612 | 6013.0537 |  | 1300 | 539.7942 | 1706.2863 | 2666.4528 |  | 1300 | 2596.0624 | 7314.9309 | 10926.6028 |  | 1300 | 1617.2278 | 5110.8433 | 7987.1179
1400 | 384.8735 | 1104.4298 | 1663.6278 | 1400 | 1557.1555 | 4384.7151 | 6546.722 |  | 1400 | 592.242 | 1873.1591 | 2927.887 |  | 1400 | 2828.7101 | 7962.669 | 11889.6482 |  | 1400 | 1775.3429 | 5613.7784 | 8775.0671
1500 | 565.0916 | 1617.8421 | 2432.5363 | 1500 | 2283.7911 | 6410.5287 | 9573.6782 |  | 1500 | 906.0494 | 2865.4592 | 4480.5429 |  | 1500 | 4144.4127 | 11648.2582 | 17391.5956 |  | 1500 | 2714.5243 | 8591.586 | 13427.4159
1600 | 602.6451 | 1721.5508 | 2586.254 | 1600 | 2443.2459 | 6851.624 | 10228.6597 |  | 1600 | 977.5824 | 3093.1311 | 4837.4157 |  | 1600 | 4431.3536 | 12442.933 | 18571.2671 |  | 1600 | 2930.1397 | 9278.3483 | 14503.3506
1800 | 975.0779 | 2772.7114 | 4160.4297 | 1800 | 3947.9294 | 11053.8947 | 16486.5763 |  | 1800 | 1678.9943 | 5317.6495 | 8315.6235 |  | 1800 | 7152.341 | 20045.2987 | 29895.6904 |  | 1800 | 5039.0197 | 15958.5877 | 24957.9746
2000 | 1329.49 | 3763.6968 | 5638.7339 | 2000 | 5368.9436 | 15024.2932 | 22383.1154 |  | 2000 | 2391.7645 | 7576.2303 | 11851.6836 |  | 2000 | 9725.8353 | 27199.5301 | 40528.8749 |  | 2000 | 7176.7981 | 22748.4993 | 35575.2517
2200 | 1706.0693 | 4808.7872 | 7191.86 | 2200 | 6879.2695 | 19212.6391 | 28615.1329 |  | 2200 | 3189.1526 | 10110.6083 | 15811.9271 |  | 2200 | 12449.7845 | 34766.3722 | 51764.9878 |  | 2200 | 9581.5098 | 30359.6033 | 47498.377
2400 | 2168.5292 | 6094.2678 | 9093.8445 | 2400 | 8726.253 | 24338.9561 | 36218.1247 |  | 2400 | 4215.5878 | 13361.4183 | 20899.4807 |  | 2400 | 15776.4978 | 43984.3296 | 65464.5652 |  | 2400 | 12658.7091 | 40125.3881 | 62765.8513
2500 | 2576.487 | 7219.9385 | 10762.8098 | 2500 | 10348.2341 | 28806.4835 | 42866.3986 |  | 2500 | 5128.0879 | 16251.2552 | 25424.9305 |  | 2500 | 18695.8175 | 52056.587 | 77448.294 |  | 2500 | 15401.6916 | 48833.5724 | 76382.025
2600 | 3067.1345 | 8568.9671 | 12766.8398 | 2600 | 12288.8107 | 34193.7146 | 50856.6832 |  | 2600 | 6263.1236 | 19841.3683 | 31043.2511 |  | 2600 | 22191.2834 | 61765.3142 | 91851.579 |  | 2600 | 18799.7766 | 59597.2142 | 93225.7665
2800 | 3868.6287 | 10764.2939 | 16010.1799 | 2800 | 15464.3017 | 42965.8309 | 63859.6037 |  | 2800 | 8200.7586 | 25971.6999 | 40628.0706 |  | 2800 | 27890.9103 | 77510.9131 | 115220.6225 |  | 2800 | 24618.6686 | 77996.5679 | 121990.0049
3000 | 4023.4628 | 11145.767 | 16549.1754 | 3000 | 16038.452 | 44494.646 | 66093.633 |  | 3000 | 8631.091 | 27318.4641 | 42725.0742 |  | 3000 | 28901.5455 | 80199.8367 | 119148.7851 |  | 3000 | 25895.9791 | 81995.0088 | 128214.4391
Re numbers according to selected fan speed
| F1S 75-170 |  |  | F1S 75-200 |  |  |  | F1S 75-230 |  |  |  | F1S 110-230 |  |  |  | F1S 110-250
| Length |  |  | Length |  |  |  | Length |  |  |  | Length |  |  |  | Length
| Lc, mm | Re |  | Lc, mm | Re |  |  | Lc, mm | Re |  |  | Lc, mm | Re |  |  | Lc, mm | Re
| 700 | 1368.1058 |  | 700 | 2024.1566 |  |  | 700 | 2224.1721 |  |  | 700 | 2824.2185 |  |  | 700 | 3848.2977
| 800 | 1368.1058 |  | 800 | 2024.1566 |  |  | 800 | 2224.1721 |  |  | 800 | 2824.2185 |  |  | 800 | 3848.2977
| 900 | 1368.1058 |  | 900 | 2024.1566 |  |  | 900 | 2224.1721 |  |  | 900 | 2824.2185 |  |  | 900 | 3848.2977
| 1000 | 2824.2185 |  | 1000 | 4184.3237 |  |  | 1000 | 4588.355 |  |  | 1000 | 5832.4512 |  |  | 1000 | 7944.6146
| 1100 | 2824.2185 |  | 1100 | 4184.3237 |  |  | 1100 | 4588.355 |  |  | 1100 | 5832.4512 |  |  | 1100 | 7944.6146
| 1200 | 2824.2185 |  | 1200 | 4184.3237 |  |  | 1200 | 4588.355 |  |  | 1200 | 5832.4512 |  |  | 1200 | 7944.6146
| 1300 | 4280.3311 |  | 1300 | 6340.4905 |  |  | 1300 | 6956.5382 |  |  | 1300 | 8836.6836 |  |  | 1300 | 12040.9315
| 1400 | 4280.3311 |  | 1400 | 6340.4905 |  |  | 1400 | 6956.5382 |  |  | 1400 | 8836.6836 |  |  | 1400 | 12040.9315
| 1500 | 5076.3927 |  | 1500 | 7512.5812 |  |  | 1500 | 8248.6381 |  |  | 1500 | 10476.8105 |  |  | 1500 | 14277.1045
| 1600 | 5076.3927 |  | 1600 | 7512.5812 |  |  | 1600 | 8248.6381 |  |  | 1600 | 10476.8105 |  |  | 1600 | 14277.1045
| 1800 | 6220.4812 |  | 1800 | 9212.7127 |  |  | 1800 | 10112.7823 |  |  | 1800 | 12844.9937 |  |  | 1800 | 17501.3539
| 2000 | 7016.5428 |  | 2000 | 10392.804 |  |  | 2000 | 11404.8823 |  |  | 2000 | 14485.1206 |  |  | 2000 | 19737.5269
| 2200 | 7720.5973 |  | 2200 | 11436.8848 |  |  | 2200 | 12552.9711 |  |  | 2200 | 15945.2335 |  |  | 2200 | 21721.6804
| 2400 | 8516.6588 |  | 2400 | 12612.9757 |  |  | 2400 | 13845.0711 |  |  | 2400 | 17581.3601 |  |  | 2400 | 23957.8534
| 2500 | 9224.7136 |  | 2500 | 13657.0565 |  |  | 2500 | 14989.1596 |  |  | 2500 | 19041.473 |  |  | 2500 | 25946.0072
| 2600 | 10016.7749 |  | 2600 | 14833.1475 |  |  | 2600 | 16281.2595 |  |  | 2600 | 20681.5999 |  |  | 2600 | 28178.1799
| 2800 | 11120.8603 |  | 2800 | 16469.2741 |  |  | 2800 | 18073.3982 |  |  | 2800 | 22957.776 |  |  | 2800 | 31282.42
| 3000 | 11120.8603 |  | 3000 | 16469.2741 |  |  | 3000 | 18073.3982 |  |  | 3000 | 22957.776 |  |  | 3000 | 31282.42
Preli
Heat output in Watts
Pressure drop in Pascal
| F1S 75-170 |  |  | F1S 75-200 |  |  |  | F1S 75-230 |  |  |  | F1S 110-230 |  |  |  | F1S 110-250
| Length | OP and ΔP |  | Length | OP and ΔP |  |  | Length | OP and ΔP |  |  | Length | OP and ΔP |  |  | Length | OP and ΔP
| Lc, mm | W | Pa | Lc, mm | W | Pa |  | Lc, mm | W | Pa |  | Lc, mm | W | Pa |  | Lc, mm | W | Pa
| 700 | 342 | 54.1454 | 700 | 506 | 189.8799 |  | 700 | 556 | 69.0023 |  | 700 | 706 | 346.9543 |  | 700 | 962 | 205.609
| 800 | 342 | 66.9026 | 800 | 506 | 249.6975 |  | 800 | 556 | 86.9943 |  | 800 | 706 | 455.9729 |  | 800 | 962 | 259.4475
| 900 | 342 | 79.3196 | 900 | 506 | 307.2642 |  | 900 | 556 | 104.8546 |  | 900 | 706 | 560.7539 |  | 900 | 962 | 312.9697
| 1000 | 706 | 348.9263 | 1000 | 1046 | 1344.3509 |  | 1000 | 1147 | 520.0729 |  | 1000 | 1458 | 2447.5936 |  | 1000 | 1986 | 1555.7587
| 1100 | 706 | 392.7108 | 1100 | 1046 | 1539.6943 |  | 1100 | 1147 | 594.9983 |  | 1100 | 1458 | 2801.592 |  | 1100 | 1986 | 1781.164
| 1200 | 706 | 435.032 | 1200 | 1046 | 1726.8373 |  | 1200 | 1147 | 669.1531 |  | 1200 | 1458 | 3140.2865 |  | 1200 | 1986 | 2004.4743
| 1300 | 1070 | 1021.421 | 1300 | 1585 | 4025.7612 |  | 1300 | 1739 | 1706.2863 |  | 1300 | 2209 | 7314.9309 |  | 1300 | 3010 | 5110.8433
| 1400 | 1070 | 1104.4298 | 1400 | 1585 | 4384.7151 |  | 1400 | 1739 | 1873.1591 |  | 1400 | 2209 | 7962.669 |  | 1400 | 3010 | 5613.7784
| 1500 | 1269 | 1617.8421 | 1500 | 1878 | 6410.5287 |  | 1500 | 2062 | 2865.4592 |  | 1500 | 2619 | 11648.2582 |  | 1500 | 3569 | 8591.586
| 1600 | 1269 | 1721.5508 | 1600 | 1878 | 6851.624 |  | 1600 | 2062 | 3093.1311 |  | 1600 | 2619 | 12442.933 |  | 1600 | 3569 | 9278.3483
| 1800 | 1555 | 2772.7114 | 1800 | 2303 | 11053.8947 |  | 1800 | 2528 | 5317.6495 |  | 1800 | 3211 | 20045.2987 |  | 1800 | 4375 | 15958.5877
| 2000 | 1754 | 3763.6968 | 2000 | 2598 | 15024.2932 |  | 2000 | 2851 | 7576.2303 |  | 2000 | 3621 | 27199.5301 |  | 2000 | 4934 | 22748.4993
| 2200 | 1930 | 4808.7872 | 2200 | 2859 | 19212.6391 |  | 2200 | 3138 | 10110.6083 |  | 2200 | 3986 | 34766.3722 |  | 2200 | 5430 | 30359.6033
| 2400 | 2129 | 6094.2678 | 2400 | 3153 | 24338.9561 |  | 2400 | 3461 | 13361.4183 |  | 2400 | 4395 | 43984.3296 |  | 2400 | 5989 | 40125.3881
| 2500 | 2306 | 7219.9385 | 2500 | 3414 | 28806.4835 |  | 2500 | 3747 | 16251.2552 |  | 2500 | 4760 | 52056.587 |  | 2500 | 6486 | 48833.5724
| 2600 | 2504 | 8568.9671 | 2600 | 3708 | 34193.7146 |  | 2600 | 4070 | 19841.3683 |  | 2600 | 5170 | 61765.3142 |  | 2600 | 7044 | 59597.2142
| 2800 | 2780 | 10764.2939 | 2800 | 4117 | 42965.8309 |  | 2800 | 4518 | 25971.6999 |  | 2800 | 5739 | 77510.9131 |  | 2800 | 7820 | 77996.5679
| 3000 | 2780 | 11145.767 | 3000 | 4117 | 44494.646 |  | 3000 | 4518 | 27318.4641 |  | 3000 | 5739 | 80199.8367 |  | 3000 | 7820 | 81995.0088
Water flow rates, L/h
F1S 75-170 |  |  |  | F1S 75-200 |  |  |  |  | F1S 75-230 |  |  |  |  | F1S 110-230 |  |  |  |  | F1S 110-250
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
700 | 16.8632 | 30.0377 | 37.5031 | 700 | 25.0314 | 44.4417 | 55.596 |  | 700 | 27.4906 | 48.8331 | 61.0414 |  | 700 | 34.8683 | 62.0075 | 77.4655 |  | 700 | 47.5157 | 84.4919 | 105.5709
800 | 16.8632 | 30.0377 | 37.5031 | 800 | 25.0314 | 44.4417 | 55.596 |  | 800 | 27.4906 | 48.8331 | 61.0414 |  | 800 | 34.8683 | 62.0075 | 77.4655 |  | 800 | 47.5157 | 84.4919 | 105.5709
900 | 16.8632 | 30.0377 | 37.5031 | 900 | 25.0314 | 44.4417 | 55.596 |  | 900 | 27.4906 | 48.8331 | 61.0414 |  | 900 | 34.8683 | 62.0075 | 77.4655 |  | 900 | 47.5157 | 84.4919 | 105.5709
1000 | 34.8683 | 62.0075 | 77.5533 | 1000 | 51.6437 | 91.8695 | 114.793 |  | 1000 | 56.65 | 100.7403 | 125.9473 |  | 1000 | 72.0201 | 128.0552 | 160.0251 |  | 1000 | 98.1054 | 174.4292 | 217.9925
1100 | 34.8683 | 62.0075 | 77.5533 | 1100 | 51.6437 | 91.8695 | 114.793 |  | 1100 | 56.65 | 100.7403 | 125.9473 |  | 1100 | 72.0201 | 128.0552 | 160.0251 |  | 1100 | 98.1054 | 174.4292 | 217.9925
1200 | 34.8683 | 62.0075 | 77.5533 | 1200 | 51.6437 | 91.8695 | 114.793 |  | 1200 | 56.65 | 100.7403 | 125.9473 |  | 1200 | 72.0201 | 128.0552 | 160.0251 |  | 1200 | 98.1054 | 174.4292 | 217.9925
1300 | 52.8733 | 93.9774 | 117.5157 | 1300 | 78.256 | 139.2096 | 173.99 |  | 1300 | 85.8971 | 152.7353 | 190.9411 |  | 1300 | 109.0841 | 194.0151 | 242.4969 |  | 1300 | 148.6952 | 264.3665 | 330.502
1400 | 52.8733 | 93.9774 | 117.5157 | 1400 | 78.256 | 139.2096 | 173.99 |  | 1400 | 85.8971 | 152.7353 | 190.9411 |  | 1400 | 109.0841 | 194.0151 | 242.4969 |  | 1400 | 148.6952 | 264.3665 | 330.502
1500 | 62.7102 | 111.4555 | 139.2974 | 1500 | 92.8357 | 164.9436 | 206.2234 |  | 1500 | 101.8821 | 181.1042 | 226.4242 |  | 1500 | 129.3727 | 230.0252 | 287.5534 |  | 1500 | 176.2736 | 313.4631 | 391.8069
1600 | 62.7102 | 111.4555 | 139.2974 | 1600 | 92.8357 | 164.9436 | 206.2234 |  | 1600 | 101.8821 | 181.1042 | 226.4242 |  | 1600 | 129.3727 | 230.0252 | 287.5534 |  | 1600 | 176.2736 | 313.4631 | 391.8069
1800 | 76.8507 | 136.5747 | 170.7403 | 1800 | 113.8269 | 202.2711 | 252.8608 |  | 1800 | 124.8934 | 222.0327 | 277.5409 |  | 1800 | 158.6199 | 282.0202 | 352.5472 |  | 1800 | 216.1481 | 384.2536 | 480.3389
2000 | 86.6876 | 154.0527 | 192.6098 | 2000 | 128.3187 | 228.1807 | 285.182 |  | 2000 | 140.8783 | 250.4016 | 313.0239 |  | 2000 | 178.9085 | 318.0302 | 397.5158 |  | 2000 | 243.7266 | 433.3502 | 541.6438
2200 | 95.3827 | 169.5107 | 211.9323 | 2200 | 141.2297 | 251.1042 | 313.9022 |  | 2200 | 155.0189 | 275.6086 | 344.4669 |  | 2200 | 196.9135 | 350.0879 | 437.566 |  | 2200 | 268.3188 | 476.9136 | 596.1859
2400 | 105.1318 | 186.9888 | 233.714 | 2400 | 155.7215 | 276.9261 | 346.1356 |  | 2400 | 171.0038 | 303.9775 | 379.9499 |  | 2400 | 217.1142 | 386.0102 | 482.5347 |  | 2400 | 295.8972 | 526.0102 | 657.4908
2500 | 113.9147 | 202.5346 | 253.1243 | 2500 | 168.7203 | 299.8495 | 374.8558 |  | 2500 | 185.1443 | 329.0967 | 411.3929 |  | 2500 | 235.2071 | 418.0679 | 522.5849 |  | 2500 | 320.4016 | 569.6614 | 712.0328
2600 | 123.7516 | 219.9248 | 274.906 | 2600 | 183.2121 | 325.6714 | 407.0892 |  | 2600 | 201.1293 | 357.4656 | 446.8759 |  | 2600 | 255.4079 | 454.0779 | 567.5535 |  | 2600 | 347.98 | 618.6702 | 773.3378
2800 | 137.3652 | 244.1657 | 305.2071 | 2800 | 203.4129 | 361.5936 | 451.97 |  | 2800 | 223.2623 | 396.8132 | 496.0604 |  | 2800 | 283.5133 | 504.0529 | 630.088 |  | 2800 | 386.3615 | 686.8258 | 858.5323
3000 | 137.3652 | 244.1657 | 305.2071 | 3000 | 203.4129 | 361.5936 | 451.97 |  | 3000 | 223.2623 | 396.8132 | 496.0604 |  | 3000 | 283.5133 | 504.0529 | 630.088 |  | 3000 | 386.3615 | 686.8258 | 858.5323
Heat output in Watts
Pressure drop in Pascal
| F1S 75-170 |  |  | F1S 75-200 |  |  |  | F1S 75-230 |  |  |  | F1S 110-230 |  |  |  | F1S 110-250
| Length | OP and Δp |  | Length | OP and Δp |  |  | Length | OP and Δp |  |  | Length | OP and Δp |  |  | Length | OP and Δp
| Lc, mm | W | Pa | Lc, mm | W | Pa |  | Lc, mm | W | Pa |  | Lc, mm | W | Pa |  | Lc, mm | W | Pa
| 700 | 342 | 54.1454 | 700 | 506 | 189.8799 |  | 700 | 556 | 69.0023 |  | 700 | 706 | 346.9543 |  | 700 | 962 | 205.609
| 800 | 342 | 66.9026 | 800 | 506 | 249.6975 |  | 800 | 556 | 86.9943 |  | 800 | 706 | 455.9729 |  | 800 | 962 | 259.4475
| 900 | 342 | 79.3196 | 900 | 506 | 307.2642 |  | 900 | 556 | 104.8546 |  | 900 | 706 | 560.7539 |  | 900 | 962 | 312.9697
| 1000 | 706 | 348.9263 | 1000 | 1046 | 1344.3509 |  | 1000 | 1147 | 520.0729 |  | 1000 | 1458 | 2447.5936 |  | 1000 | 1986 | 1555.7587
| 1100 | 706 | 392.7108 | 1100 | 1046 | 1539.6943 |  | 1100 | 1147 | 594.9983 |  | 1100 | 1458 | 2801.592 |  | 1100 | 1986 | 1781.164
| 1200 | 706 | 435.032 | 1200 | 1046 | 1726.8373 |  | 1200 | 1147 | 669.1531 |  | 1200 | 1458 | 3140.2865 |  | 1200 | 1986 | 2004.4743
| 1300 | 1070 | 1021.421 | 1300 | 1585 | 4025.7612 |  | 1300 | 1739 | 1706.2863 |  | 1300 | 2209 | 7314.9309 |  | 1300 | 3010 | 5110.8433
| 1400 | 1070 | 1104.4298 | 1400 | 1585 | 4384.7151 |  | 1400 | 1739 | 1873.1591 |  | 1400 | 2209 | 7962.669 |  | 1400 | 3010 | 5613.7784
| 1500 | 1269 | 1617.8421 | 1500 | 1878 | 6410.5287 |  | 1500 | 2062 | 2865.4592 |  | 1500 | 2619 | 11648.2582 |  | 1500 | 3569 | 8591.586
| 1600 | 1269 | 1721.5508 | 1600 | 1878 | 6851.624 |  | 1600 | 2062 | 3093.1311 |  | 1600 | 2619 | 12442.933 |  | 1600 | 3569 | 9278.3483
| 1800 | 1555 | 2772.7114 | 1800 | 2303 | 11053.8947 |  | 1800 | 2528 | 5317.6495 |  | 1800 | 3211 | 20045.2987 |  | 1800 | 4375 | 15958.5877
| 2000 | 1754 | 3763.6968 | 2000 | 2598 | 15024.2932 |  | 2000 | 2851 | 7576.2303 |  | 2000 | 3621 | 27199.5301 |  | 2000 | 4934 | 22748.4993
| 2200 | 1930 | 4808.7872 | 2200 | 2859 | 19212.6391 |  | 2200 | 3138 | 10110.6083 |  | 2200 | 3986 | 34766.3722 |  | 2200 | 5430 | 30359.6033
| 2400 | 2129 | 6094.2678 | 2400 | 3153 | 24338.9561 |  | 2400 | 3461 | 13361.4183 |  | 2400 | 4395 | 43984.3296 |  | 2400 | 5989 | 40125.3881
| 2500 | 2306 | 7219.9385 | 2500 | 3414 | 28806.4835 |  | 2500 | 3747 | 16251.2552 |  | 2500 | 4760 | 52056.587 |  | 2500 | 6486 | 48833.5724
| 2600 | 2504 | 8568.9671 | 2600 | 3708 | 34193.7146 |  | 2600 | 4070 | 19841.3683 |  | 2600 | 5170 | 61765.3142 |  | 2600 | 7044 | 59597.2142
| 2800 | 2780 | 10764.2939 | 2800 | 4117 | 42965.8309 |  | 2800 | 4518 | 25971.6999 |  | 2800 | 5739 | 77510.9131 |  | 2800 | 7820 | 77996.5679
| 3000 | 2780 | 11145.767 | 3000 | 4117 | 44494.646 |  | 3000 | 4518 | 27318.4641 |  | 3000 | 5739 | 80199.8367 |  | 3000 | 7820 | 81995.0088

## F2C+F2V Heating
AQUILO F2C and F2V | [11 empty] | 070721 MII
Re corrected heat outputs
Re corrected flow resistances
ΔT according to DIN 4703-3: |  |  |  | Tflow = | 75 | oC |  | Fan speed = | 2 | Select 1, 2 or 3
|  |  |  | Trtn = | 65 | oC |  | Design recommendation, fan spee 2
|  |  |  | Tin = | 20 | oC
|  |  |  | ΔTar = | 50 | K |  |  |  | High flow resistance
Standard heat outputs at ΔT50K
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 501 | 890 | 1113 | 850 | 776 | 1380 | 1725 |  | 850 | 942 | 1675 | 2094 | Error
1200 | 1001 | 1780 | 2225 | 1200 | 1553 | 2760 | 3450 |  | 1200 | 1885 | 3351 | 4189 | Error
1600 | 1487 | 2644 | 3305 | 1600 | 2306 | 4099 | 5124 |  | 1600 | 2800 | 4978 | 6222 | Error
2100 | 2120 | 3770 | 4712 | 2100 | 3288 | 5845 | 7306 |  | 2100 | 3992 | 7096 | 8870 | Error
2400 | 2592 | 4607 | 5759 | 2400 | 4018 | 7143 | 8929 |  | 2400 | 4879 | 8674 | 10842 | Error
2700 | 3107 | 5524 | 6905 | 2700 | 4817 | 8564 | 10705 |  | 2700 | 5849 | 10398 | 12998 | Error
Reynolds numbers at standard output conditions 75/65/20
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 2004.155 | 3560.2754 | 4452.3444 | 850 | 2069.4934 | 3680.2847 | 4600.3559 |  | 850 | 2512.1943 | 4467.0122 | 5584.432
1200 | 4004.3098 | 7120.5508 | 8900.6886 | 1200 | 4141.6537 | 7360.5694 | 9200.7118 |  | 1200 | 5027.0556 | 8936.6913 | 11171.5309
1600 | 5948.4602 | 10576.8182 | 13221.0228 | 1600 | 6149.8091 | 10931.5123 | 13665.0571 |  | 1600 | 7467.2443 | 13275.6937 | 16593.2837
2100 | 8480.6561 | 15081.1667 | 18849.4582 | 2100 | 8768.6783 | 15587.8725 | 19484.174 |  | 2100 | 10646.1569 | 18924.1306 | 23655.1633
2400 | 10368.8021 | 18429.4257 | 23037.7822 | 2400 | 10715.4956 | 19049.4737 | 23812.5088 |  | 2400 | 13011.6732 | 23132.4562 | 28914.2368
2700 | 12428.9615 | 22097.7095 | 27622.1368 | 2700 | 12846.3271 | 22839.1002 | 28548.8752 |  | 2700 | 15598.54 | 27730.1452 | 34664.0149
Heat outputs at calculation conditions without correction
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 501 | 890 | 1113 | 850 | 776 | 1380 | 1725 |  | 850 | 942 | 1675 | 2094
1200 | 1001 | 1780 | 2225 | 1200 | 1553 | 2760 | 3450 |  | 1200 | 1885 | 3351 | 4189
1600 | 1487 | 2644 | 3305 | 1600 | 2306 | 4099 | 5124 |  | 1600 | 2800 | 4978 | 6222
2100 | 2120 | 3770 | 4712 | 2100 | 3288 | 5845 | 7306 |  | 2100 | 3992 | 7096 | 8870
2400 | 2592 | 4607 | 5759 | 2400 | 4018 | 7143 | 8929 |  | 2400 | 4879 | 8674 | 10842
2700 | 3107 | 5524 | 6905 | 2700 | 4817 | 8564 | 10705 |  | 2700 | 5849 | 10398 | 12998
Reynolds numbers at Twater=70 and (Tflow-Trtn) according to calculation values
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 2004.155 | 3560.2754 | 4452.3444 | 850 | 2069.4934 | 3680.2847 | 4600.3559 |  | 850 | 2512.1943 | 4467.0122 | 5584.432
1200 | 4004.3098 | 7120.5508 | 8900.6886 | 1200 | 4141.6537 | 7360.5694 | 9200.7118 |  | 1200 | 5027.0556 | 8936.6913 | 11171.5309
1600 | 5948.4602 | 10576.8182 | 13221.0228 | 1600 | 6149.8091 | 10931.5123 | 13665.0571 |  | 1600 | 7467.2443 | 13275.6937 | 16593.2837
2100 | 8480.6561 | 15081.1667 | 18849.4582 | 2100 | 8768.6783 | 15587.8725 | 19484.174 |  | 2100 | 10646.1569 | 18924.1306 | 23655.1633
2400 | 10368.8021 | 18429.4257 | 23037.7822 | 2400 | 10715.4956 | 19049.4737 | 23812.5088 |  | 2400 | 13011.6732 | 23132.4562 | 28914.2368
2700 | 12428.9615 | 22097.7095 | 27622.1368 | 2700 | 12846.3271 | 22839.1002 | 28548.8752 |  | 2700 | 15598.54 | 27730.1452 | 34664.0149
Reynolds numbers at calculation conditions
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 2004.155 | 3560.2754 | 4452.3444 | 850 | 2069.4934 | 3680.2847 | 4600.3559 |  | 850 | 2512.1943 | 4467.0122 | 5584.432
1200 | 4004.3098 | 7120.5508 | 8900.6886 | 1200 | 4141.6537 | 7360.5694 | 9200.7118 |  | 1200 | 5027.0556 | 8936.6913 | 11171.5309
1600 | 5948.4602 | 10576.8182 | 13221.0228 | 1600 | 6149.8091 | 10931.5123 | 13665.0571 |  | 1600 | 7467.2443 | 13275.6937 | 16593.2837
2100 | 8480.6561 | 15081.1667 | 18849.4582 | 2100 | 8768.6783 | 15587.8725 | 19484.174 |  | 2100 | 10646.1569 | 18924.1306 | 23655.1633
2400 | 10368.8021 | 18429.4257 | 23037.7822 | 2400 | 10715.4956 | 19049.4737 | 23812.5088 |  | 2400 | 13011.6732 | 23132.4562 | 28914.2368
2700 | 12428.9615 | 22097.7095 | 27622.1368 | 2700 | 12846.3271 | 22839.1002 | 28548.8752 |  | 2700 | 15598.54 | 27730.1452 | 34664.0149
Re corrected heat outputs - W
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 501 | 890 | 1113 | 850 | 776 | 1380 | 1725 |  | 850 | 942 | 1675 | 2094
1200 | 1001 | 1780 | 2225 | 1200 | 1553 | 2760 | 3450 |  | 1200 | 1885 | 3351 | 4189
1600 | 1487 | 2644 | 3305 | 1600 | 2306 | 4099 | 5124 |  | 1600 | 2800 | 4978 | 6222
2100 | 2120 | 3770 | 4712 | 2100 | 3288 | 5845 | 7306 |  | 2100 | 3992 | 7096 | 8870
2400 | 2592 | 4607 | 5759 | 2400 | 4018 | 7143 | 8929 |  | 2400 | 4879 | 8674 | 10842
2700 | 3107 | 5524 | 6905 | 2700 | 4817 | 8564 | 10705 |  | 2700 | 5849 | 10398 | 12998
Flow resistance / Pressure drop - Pa
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 230.3883 | 733.6848 | 1151.4756 | 850 | 429.9459 | 1075.6072 | 1534.676 |  | 850 | 585.4833 | 1464.4319 | 2089.8483
1200 | 1681.8764 | 5318.9501 | 8311.3046 | 1200 | 2821.4168 | 6965.3816 | 9891.105 |  | 1200 | 3825.5876 | 9448.7196 | 13418.7974
1600 | 5561.2464 | 17509.4886 | 27314.656 | 1600 | 8048.4825 | 19692.5457 | 27866.114 |  | 1600 | 10885.2646 | 26640.8795 | 37690.8439
2100 | 16835.624 | 53210.3899 | 83105.5183 | 2100 | 20081.125 | 48921.3931 | 69098.5242 |  | 2100 | 27114.3939 | 66048.7819 | 93294.8713
2400 | 31823.0815 | 101173.3821 | 158487.1644 | 2400 | 33255.4089 | 81113.2758 | 114628.9121 |  | 2400 | 44929.9624 | 109595.675 | 154862.3209
2700 | 58666.691 | 188594.9736 | 296610.2885 | 2700 | 53594.0488 | 131256.1536 | 185768.9778 |  | 2700 | 72501.7756 | 177542.4526 | 251293.78
Re numbers according to selected fan speed
| F2C 110-230 |  |  | F2C 170-340 |  |  |  | F2V 170-340
| Length |  |  | Length |  |  |  | Length
| Lc, mm | Re |  | Lc, mm | Re |  |  | Lc, mm | Re
| 850 | 3560.2754 |  | 850 | 3680.2847 |  |  | 850 | 4467.0122
| 1200 | 7120.5508 |  | 1200 | 7360.5694 |  |  | 1200 | 8936.6913
| 1600 | 10576.8182 |  | 1600 | 10931.5123 |  |  | 1600 | 13275.6937
| 2100 | 15081.1667 |  | 2100 | 15587.8725 |  |  | 2100 | 18924.1306
| 2400 | 18429.4257 |  | 2400 | 19049.4737 |  |  | 2400 | 23132.4562
| 2700 | 22097.7095 |  | 2700 | 22839.1002 |  |  | 2700 | 27730.1452
Heat output in Watts
Pressure drop in Pascal
| F2C 110-230 |  |  | F2C 170-340 |  |  |  | F2V 170-340
| Length | OP and Δp |  | Length | OP and Δp |  |  | Length | OP and Δp
| Lc, mm | W | Pa | Lc, mm | W | Pa |  | Lc, mm | W | Pa
| 850 | 890 | 733.6848 | 850 | 1380 | 1075.6072 |  | 850 | 1675 | 1464.4319
| 1200 | 1780 | 5318.9501 | 1200 | 2760 | 6965.3816 |  | 1200 | 3351 | 9448.7196
| 1600 | 2644 | 17509.4886 | 1600 | 4099 | 19692.5457 |  | 1600 | 4978 | 26640.8795
| 2100 | 3770 | 53210.3899 | 2100 | 5845 | 48921.3931 |  | 2100 | 7096 | 66048.7819
| 2400 | 4607 | 101173.3821 | 2400 | 7143 | 81113.2758 |  | 2400 | 8674 | 109595.675
| 2700 | 5524 | 188594.9736 | 2700 | 8564 | 131256.1536 |  | 2700 | 10398 | 177542.4526
Water flow ratesa, L/h
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 44.0025 | 78.1682 | 97.7541 | 850 | 68.1556 | 121.2046 | 151.5057 |  | 850 | 82.7353 | 147.1142 | 183.9147
1200 | 87.9172 | 156.3363 | 195.4204 | 1200 | 136.399 | 242.4091 | 303.0114 |  | 1200 | 165.5584 | 294.3163 | 367.9173
1600 | 130.6023 | 232.2209 | 290.2761 | 1600 | 202.5346 | 360.0127 | 450.0378 |  | 1600 | 245.9223 | 437.2147 | 546.4745
2100 | 186.1983 | 331.1168 | 413.8521 | 2100 | 288.783 | 513.3628 | 641.6815 |  | 2100 | 350.6149 | 623.2373 | 779.0467
2400 | 227.6538 | 404.63 | 505.8094 | 2400 | 352.8985 | 627.3653 | 784.2286 |  | 2400 | 428.5196 | 761.8321 | 952.2462
2700 | 272.8859 | 485.1695 | 606.4619 | 2700 | 423.0742 | 752.1709 | 940.2136 |  | 2700 | 513.7141 | 913.25 | 1141.6064

## F2C+F2V Cooling
AQUILO F2C and F2V - COOLING | [11 empty] | 070721 MII
Re corrected cooling outputs
Re corrected flow resistances
ΔT according to DIN 4703-3: |  |  |  | Tflow = | 8 | oC |  | Fan speed = | 2 | Select 1, 2 or 3
|  |  |  | Trtn = | 14 | oC |  | Design recommendation, fan speed 2
|  |  |  | Tin = | 28 | oC
|  |  |  | ΔTar = | 17 | K |  |  |  | High flow resistance
Standard cooling outputs at ΔT17K
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 128 | 227 | 284 | 850 | 198 | 352 | 440 |  | 850 | 293 | 522 | 652 | Error
1200 | 255 | 454 | 567 | 1200 | 396 | 705 | 881 |  | 1200 | 586 | 1042 | 1303 | Error
1600 | 379 | 674 | 843 | 1600 | 589 | 1046 | 1308 |  | 1600 | 871 | 1549 | 1936 | Error
2100 | 541 | 962 | 1202 | 2100 | 839 | 1492 | 1865 |  | 2100 | 1242 | 2208 | 2760 | Error
2400 | 661 | 1175 | 1469 | 2400 | 1026 | 1823 | 2279 |  | 2400 | 1518 | 2699 | 3374 | Error
2700 | 792 | 1409 | 1761 | 2700 | 1230 | 2186 | 2733 |  | 2700 | 1820 | 3236 | 4045 | Error
Reynolds numbers at standard/table conditions 8/14/28 dC
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 285.0833 | 505.5775 | 632.5286 | 850 | 293.9922 | 522.6528 | 653.316 |  | 850 | 435.049 | 775.0703 | 968.0955
1200 | 567.9394 | 1011.1549 | 1262.83 | 1200 | 587.9844 | 1046.7903 | 1308.1167 |  | 1200 | 870.0981 | 1547.171 | 1934.7061
1600 | 844.1139 | 1501.1419 | 1877.541 | 1600 | 874.5525 | 1553.1102 | 1942.1301 |  | 1600 | 1293.2686 | 2299.9691 | 2874.5902
2100 | 1204.9225 | 2142.5794 | 2677.1106 | 2100 | 1245.7547 | 2215.335 | 2769.1687 |  | 2100 | 1844.1328 | 3278.4582 | 4098.0728
2400 | 1472.1881 | 2616.9758 | 3271.7766 | 2400 | 1523.414 | 2706.8068 | 3383.8797 |  | 2400 | 2253.94 | 4007.4994 | 5009.7455
2700 | 1763.9531 | 3138.1438 | 3922.1229 | 2700 | 1826.315 | 3245.7924 | 4057.9829 |  | 2700 | 2702.3523 | 4804.8419 | 6006.0523
Cooling outputs at calculation conditions without correction
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 128 | 227 | 284 | 850 | 198 | 352 | 440 |  | 850 | 293 | 522 | 652
1200 | 255 | 454 | 567 | 1200 | 396 | 705 | 881 |  | 1200 | 586 | 1042 | 1303
1600 | 379 | 674 | 843 | 1600 | 589 | 1046 | 1308 |  | 1600 | 871 | 1549 | 1936
2100 | 541 | 962 | 1202 | 2100 | 839 | 1492 | 1865 |  | 2100 | 1242 | 2208 | 2760
2400 | 661 | 1175 | 1469 | 2400 | 1026 | 1823 | 2279 |  | 2400 | 1518 | 2699 | 3374
2700 | 792 | 1409 | 1761 | 2700 | 1230 | 2186 | 2733 |  | 2700 | 1820 | 3236 | 4045
Reynolds numbers at Twater=70 and (Tflow-Trtn) according to calculation values
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 853.3994 | 1513.4504 | 1893.4798 | 850 | 880.0681 | 2346.8482 | 2933.5603 |  | 850 | 1302.323 | 2320.1795 | 2898.002
1200 | 1700.1315 | 3026.9008 | 3780.2924 | 1200 | 2640.2042 | 4700.3636 | 5873.7877 |  | 1200 | 2604.6459 | 4631.4694 | 5791.5591
1600 | 2526.8621 | 4493.681 | 5620.4348 | 1600 | 3926.9705 | 6973.8728 | 8720.6746 |  | 1600 | 3871.4106 | 6884.9771 | 8605.1101
2100 | 3606.9457 | 6413.8295 | 8013.9533 | 2100 | 5593.7661 | 9947.4362 | 12434.2952 |  | 2100 | 5520.4271 | 9814.0926 | 12267.6157
2400 | 4407.0076 | 7833.9394 | 9794.091 | 2400 | 6840.5292 | 12154.2736 | 15194.5088 |  | 2400 | 6747.1886 | 11996.4836 | 14996.7157
2700 | 5280.4085 | 9394.0601 | 11740.9083 | 2700 | 8200.6344 | 14574.4608 | 18221.4096 |  | 2700 | 8089.5147 | 14383.3349 | 17979.1686
Reynolds numbers at calculation conditions
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 285.0833 | 505.5775 | 632.5286 | 850 | 293.9922 | 522.6528 | 653.316 |  | 850 | 435.049 | 775.0703 | 968.0955
1200 | 567.9394 | 1011.1549 | 1262.83 | 1200 | 587.9844 | 1046.7903 | 1308.1167 |  | 1200 | 870.0981 | 1547.171 | 1934.7061
1600 | 844.1139 | 1501.1419 | 1877.541 | 1600 | 874.5525 | 1553.1102 | 1942.1301 |  | 1600 | 1293.2686 | 2299.9691 | 2874.5902
2100 | 1204.9225 | 2142.5794 | 2677.1106 | 2100 | 1245.7547 | 2215.335 | 2769.1687 |  | 2100 | 1844.1328 | 3278.4582 | 4098.0728
2400 | 1472.1881 | 2616.9758 | 3271.7766 | 2400 | 1523.414 | 2706.8068 | 3383.8797 |  | 2400 | 2253.94 | 4007.4994 | 5009.7455
2700 | 1763.9531 | 3138.1438 | 3922.1229 | 2700 | 1826.315 | 3245.7924 | 4057.9829 |  | 2700 | 2702.3523 | 4804.8419 | 6006.0523
Re corrected heat outputs - W
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 128 | 227 | 284 | 850 | 198 | 352 | 440 |  | 850 | 293 | 522 | 652
1200 | 255 | 454 | 567 | 1200 | 396 | 705 | 881 |  | 1200 | 586 | 1042 | 1303
1600 | 379 | 674 | 843 | 1600 | 589 | 1046 | 1308 |  | 1600 | 871 | 1549 | 1936
2100 | 541 | 962 | 1202 | 2100 | 839 | 1492 | 1865 |  | 2100 | 1242 | 2208 | 2760
2400 | 661 | 1175 | 1469 | 2400 | 1026 | 1823 | 2279 |  | 2400 | 1518 | 2699 | 3374
2700 | 792 | 1409 | 1761 | 2700 | 1230 | 2186 | 2733 |  | 2700 | 1820 | 3236 | 4045
Flow resistance / Pressure drop - Pa
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 118.3488 | 375.6024 | 589.9988 | 850 | 319.0244 | 1129.5314 | 868.4906 |  | 850 | 595.567 | 1458.8911 | 1118.6583
1200 | 870.7145 | 1316.113 | 1764.9905 | 1200 | 2158.8687 | 2789.741 | 3385.8433 |  | 1200 | 2766.2815 | 3472.1678 | 4217.2005
1600 | 2214.162 | 3323.8149 | 4438.2775 | 1600 | 3702.3067 | 6043.285 | 7282.2105 |  | 1600 | 4580.5361 | 7488.7593 | 16807.2836
2100 | 3706.2808 | 7836.8098 | 16035.0428 | 2100 | 7256.7853 | 11692.877 | 23623.068 |  | 2100 | 8961.2958 | 31967.2772 | 44632.5607
2400 | 6030.7654 | 18439.4155 | 37587.5798 | 2400 | 10410.3061 | 26460.6543 | 45184.5471 |  | 2400 | 12861.2435 | 52420.647 | 73259.5264
2700 | 9635.5254 | 44114.4065 | 68552.677 | 2700 | 14635.9821 | 51583.7166 | 71903.6835 |  | 2700 | 28614.5849 | 83776.3056 | 117282.5959
Re numbers according to selected fan speed
| F2C 110-230 |  |  | F2C 170-340 |  |  |  | F2V 170-340
| Length |  |  | Length |  |  |  | Length
| Lc, mm | Re |  | Lc, mm | Re |  |  | Lc, mm | Re
| 850 | 505.5775 |  | 850 | 522.6528 |  |  | 850 | 775.0703
| 1200 | 1011.1549 |  | 1200 | 1046.7903 |  |  | 1200 | 1547.171
| 1600 | 1501.1419 |  | 1600 | 1553.1102 |  |  | 1600 | 2299.9691
| 2100 | 2142.5794 |  | 2100 | 2215.335 |  |  | 2100 | 3278.4582
| 2400 | 2616.9758 |  | 2400 | 2706.8068 |  |  | 2400 | 4007.4994
| 2700 | 3138.1438 |  | 2700 | 3245.7924 |  |  | 2700 | 4804.8419
Cooling output in Watts
Pressure drop in Pascal
| F2C 110-230 |  |  | F2C 170-340 |  |  |  | F2V 170-340
| Length | OP and Δp |  | Length | OP and Δp |  |  | Length | OP and Δp
| Lc, mm | W | Pa | Lc, mm | W | Pa |  | Lc, mm | W | Pa
| 850 | 227 | 375.6024 | 850 | 352 | 1129.5314 |  | 850 | 522 | 1458.8911
| 1200 | 454 | 1316.113 | 1200 | 705 | 2789.741 |  | 1200 | 1042 | 3472.1678
| 1600 | 674 | 3323.8149 | 1600 | 1046 | 6043.285 |  | 1600 | 1549 | 7488.7593
| 2100 | 962 | 7836.8098 | 2100 | 1492 | 11692.877 |  | 2100 | 2208 | 31967.2772
| 2400 | 1175 | 18439.4155 | 2400 | 1823 | 26460.6543 |  | 2400 | 2699 | 52420.647
| 2700 | 1409 | 44114.4065 | 2700 | 2186 | 51583.7166 |  | 2700 | 3236 | 83776.3056
Water flow ratesa, L/h
F2C 110-230 |  |  |  | F2C 170-340 |  |  |  |  | F2V 170-340
Length |  | Fan speed |  | Length |  | Fan speed |  |  | Length |  | Fan speed
Lc, mm | 1 | 2 | 3 | Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
850 | 18.3544 | 32.5504 | 40.7238 | 850 | 28.392 | 50.4746 | 63.0932 |  | 850 | 42.0144 | 74.8515 | 93.4927
1200 | 36.5654 | 65.1007 | 81.3042 | 1200 | 56.7839 | 101.0926 | 126.3299 |  | 1200 | 84.0287 | 149.4162 | 186.842
1600 | 54.3462 | 96.6474 | 120.8809 | 1600 | 84.4589 | 149.9898 | 187.559 |  | 1600 | 124.8959 | 222.1168 | 277.6102
2100 | 77.576 | 137.9447 | 172.3592 | 2100 | 120.3073 | 213.9434 | 267.4293 |  | 2100 | 178.095 | 316.6133 | 395.7666
2400 | 94.7832 | 168.4876 | 210.6453 | 2400 | 147.1219 | 261.4067 | 326.7942 |  | 2400 | 217.6716 | 387.0196 | 483.8104
2700 | 113.5678 | 202.0417 | 252.5163 | 2700 | 176.3743 | 313.4586 | 391.895 |  | 2700 | 260.9765 | 464.022 | 580.0275

## F4C+F4V Heating
AQUILO F4C and F4V | [11 empty] | 070721 MII
Re corrected heat outputs
Re corrected flow resistances
ΔT according to DIN 4703-3: |  |  |  | Tflow = | 55 | oC |  | Fan speed = | 2 | Select 1, 2 or 3
|  |  |  | Trtn = | 35 | oC |  | Design recommendation, fan speed 2
|  |  |  | Tin = | 20 | oC
|  |  |  | ΔTln = | 23.6045 | K |  |  |  | High flow resistance
Standard heat outputs at ΔT50K
| F4C 170-340 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 524 | 932 | 1165 |  | 850 | 637 | 1132 | 1415 |  |  |  | Error
| 1200 | 1049 | 1865 | 2331 |  | 1200 | 1274 | 2264 | 2830 |  |  |  | Error
| 1600 | 1558 | 2770 | 3462 |  | 1600 | 1892 | 3363 | 4204 |  |  |  | Error
| 2100 | 2221 | 3949 | 4936 |  | 2100 | 2697 | 4795 | 5994 |  |  |  | Error
| 2400 | 2715 | 4826 | 6033 |  | 2400 | 3296 | 5860 | 7325 |  |  |  | Error
| 2700 | 3255 | 5786 | 7233 |  | 2700 | 3952 | 7026 | 8782 |  |  |  | Error
Reynolds numbers at standard output conditions 75/65/20
| F4C 170-340 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 1397.4414 | 2485.5256 | 3106.907 |  | 850 | 1698.7981 | 3018.9002 | 3773.6253
| 1200 | 2797.5498 | 4973.7181 | 6216.4809 |  | 1200 | 3397.5962 | 6037.8004 | 7547.2505
| 1600 | 4154.9881 | 7387.2381 | 9232.7142 |  | 1600 | 5045.7237 | 8968.6938 | 11211.534
| 2100 | 5923.1249 | 10531.4814 | 13163.685 |  | 2100 | 7192.5564 | 12787.6559 | 15985.2366
| 2400 | 7240.5601 | 12870.329 | 16089.2447 |  | 2400 | 8790.0133 | 15627.8756 | 19534.8445
| 2700 | 8680.6715 | 15430.527 | 19289.4922 |  | 2700 | 10539.482 | 18737.4495 | 23420.4785
Heat outputs at calculation conditions without correction
| F2C 110-230 |  |  |  |  | F2C 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 229.4867 | 408.171 | 510.2138 |  | 850 | 278.9753 | 495.7614 | 619.7017
| 1200 | 459.4114 | 816.78 | 1020.8655 |  | 1200 | 557.9505 | 991.5228 | 1239.4035
| 1600 | 682.3288 | 1213.1264 | 1516.189 |  | 1600 | 828.6047 | 1472.8317 | 1841.1492
| 2100 | 972.6908 | 1729.4715 | 2161.7299 |  | 2100 | 1181.1559 | 2099.9787 | 2625.0828
| 2400 | 1189.039 | 2113.5552 | 2642.1629 |  | 2400 | 1443.489 | 2566.3973 | 3207.9966
| 2700 | 1425.533 | 2533.9888 | 3167.705 |  | 2700 | 1730.7853 | 3077.049 | 3846.0923
Reynolds numbers at Twater=70 and (Tflow-Trtn) according to calculation values
| F4C 170-340 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 306.006 | 544.2702 | 680.3377 |  | 850 | 371.9958 | 661.0663 | 826.3329
| 1200 | 612.5959 | 1089.1243 | 1361.2594 |  | 1200 | 743.9916 | 1322.1326 | 1652.6658
| 1600 | 909.8422 | 1617.627 | 2021.7417 |  | 1600 | 1104.8918 | 1963.9276 | 2455.0555
| 2100 | 1297.0215 | 2306.1404 | 2882.5295 |  | 2100 | 1574.9963 | 2800.1882 | 3500.3812
| 2400 | 1585.508 | 2818.2916 | 3523.1565 |  | 2400 | 1924.8009 | 3422.1278 | 4277.6597
| 2700 | 1900.8577 | 3378.9132 | 4223.9335 |  | 2700 | 2307.8923 | 4103.0494 | 5128.5198
Reynolds numbers at calculation conditions
| F4C 170-340 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 222.885 | 396.429 | 495.5362 |  | 850 | 270.9499 | 481.4996 | 601.8745
| 1200 | 446.1953 | 793.2833 | 991.4978 |  | 1200 | 541.8997 | 962.9992 | 1203.749
| 1600 | 662.7 | 1178.2278 | 1472.572 |  | 1600 | 804.7679 | 1430.4621 | 1788.184
| 2100 | 944.709 | 1679.719 | 2099.5424 |  | 2100 | 1147.177 | 2039.5676 | 2549.5658
| 2400 | 1154.8334 | 2052.7535 | 2566.1546 |  | 2400 | 1401.9635 | 2492.5685 | 3115.7106
| 2700 | 1384.524 | 2461.0924 | 3076.5782 |  | 2700 | 1680.995 | 2988.5301 | 3735.4499
Re corrected heat outputs - W
| F4C 170-340 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 171.4338 | 312.5077 | 393.947 |  | 850 | 210.2526 | 382.3835 | 481.8126
| 1200 | 353.3403 | 640.925 | 806.6733 |  | 1200 | 432.2017 | 782.7913 | 984.9992
| 1600 | 532.2558 | 963.5177 | 1211.8305 |  | 1600 | 650.5041 | 1176.2358 | 1479.2434
| 2100 | 767.4725 | 1387.2245 | 1743.9892 |  | 2100 | 937.3957 | 1692.9292 | 2127.9648
| 2400 | 943.8353 | 1704.1527 | 2142.145 |  | 2400 | 1152.1589 | 2079.2565 | 2612.8035
| 2700 | 1137.4303 | 2052.3668 | 2579.2357 |  | 2700 | 1388.3064 | 2503.7364 | 3145.3584
Flow resistance / Pressure drop - Pa
| F4C 170-340 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 17.2125 | 51.5768 | 78.756 |  | 850 | 24.9957 | 74.5822 | 113.7896 |  | < 50 | 51.5768 | 78.756 | < 50 | 74.5822 | 113.7896
| 1200 | 140.8502 | 403.4949 | 605.8804 |  | 1200 | 201.0921 | 574.5384 | 862.3628 |  | 140.8502 | 403.4949 | 605.8804 | 201.0921 | 574.5384 | 862.3628
| 1600 | 408.9887 | 1139.4008 | 1692.7655 |  | 1600 | 578.2734 | 1607.8445 | 1978.422 |  | 408.9887 | 1139.4008 | 1692.7655 | 578.2734 | 1607.8445 | 1978.422
| 2100 | 1025.7844 | 2817.7251 | 2237.4347 |  | 2100 | 1446.1033 | 2296.9474 | 3430.2334
| 2400 | 1758.0347 | 2770.7403 | 4284.6469 |  | 2400 | 2484.2795 | 3823.9482 | 8271.2679
| 2700 | 3019.9048 | 4611.1988 | 10335.0986 |  | 2700 | 4259.9541 | 9737.7559 | 14629.1227
Re numbers according to selected fan speed
|  | F4C 170-340 |  |  |  | F4V 170-340
|  | Length |  |  |  | Length
|  | Lc, mm | Re |  |  | Lc, mm | Re
|  | 850 | 396.429 |  |  | 850 | 481.4996
|  | 1200 | 793.2833 |  |  | 1200 | 962.9992
|  | 1600 | 1178.2278 |  |  | 1600 | 1430.4621
|  | 2100 | 1679.719 |  |  | 2100 | 2039.5676
|  | 2400 | 2052.7535 |  |  | 2400 | 2492.5685
|  | 2700 | 2461.0924 |  |  | 2700 | 2988.5301
Heat output in Watts
Pressure drop in Pascal
|  | F4C 170-340 |  |  |  | F4V 170-340
|  | Length | OP and Δp |  |  | Length | OP and Δp
|  | Lc, mm | W | Pa |  | Lc, mm | W | Pa
|  | 850 | 312.5077 | 51.5768 |  | 850 | 382.3835 | 74.5822
|  | 1200 | 640.925 | 403.4949 |  | 1200 | 782.7913 | 574.5384
|  | 1600 | 963.5177 | 1139.4008 |  | 1600 | 1176.2358 | 1607.8445
|  | 2100 | 1387.2245 | 2817.7251 |  | 2100 | 1692.9292 | 2296.9474
|  | 2400 | 1704.1527 | 2770.7403 |  | 2400 | 2079.2565 | 3823.9482
|  | 2700 | 2052.3668 | 4611.1988 |  | 2700 | 2503.7364 | 9737.7559
Water flow rates, L/h
| F4C 110-230 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 7.4402 | 13.5627 | 17.0971 |  | 850 | 9.1249 | 16.5953 | 20.9105
| 1200 | 15.3348 | 27.8159 | 35.0093 |  | 1200 | 18.7574 | 33.9728 | 42.7485
| 1600 | 23.0997 | 41.8162 | 52.5929 |  | 1600 | 28.2316 | 51.0481 | 64.1985
| 2100 | 33.308 | 60.2049 | 75.6884 |  | 2100 | 40.6826 | 73.4724 | 92.3527
| 2400 | 40.962 | 73.9595 | 92.9681 |  | 2400 | 50.0032 | 90.2388 | 113.3945
| 2700 | 49.364 | 89.0718 | 111.9377 |  | 2700 | 60.2519 | 108.6611 | 136.5072

## F4C+F4V Cooling
AQUILO F4C and F4V - COOLING | [10 empty] | 070721 MII
Re corrected cooling outputs
Re corrected flow resistances
ΔT according to DIN 4703-3: |  |  |  | Tflow = | 14 | oC |  | Fan speed = | 2 | Select 1, 2 or 3
|  |  |  | Trtn = | 20 | oC |  | Design recommendation, fan speed 2
|  |  |  | Tin = | 25 | oC
|  |  |  | ΔTln = | 7.6098 | K |  |  |  | High flow resistance
Standard cooling outputs at ΔT17K
| F4C 170-340 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 198 | 352 | 440 |  | 850 | 293 | 522 | 652 |  |  | Error
| 1200 | 396 | 705 | 881 |  | 1200 | 586 | 1042 | 1303 |  |  | Error
| 1600 | 589 | 1046 | 1308 |  | 1600 | 871 | 1549 | 1936 |  |  | Error
| 2100 | 839 | 1492 | 1865 |  | 2100 | 1242 | 2208 | 2760 |  |  | Error
| 2400 | 1026 | 1823 | 2279 |  | 2400 | 1518 | 2699 | 3374 |  |  | Error
| 2700 | 1230 | 2186 | 2733 |  | 2700 | 1820 | 3236 | 4045 |  |  | Error
Reynolds numbers at standard output conditions 8/14/28
| F4C 170-340 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 293.9922 | 522.6528 | 653.316 |  | 850 | 435.049 | 775.0703 | 968.0955
| 1200 | 587.9844 | 1046.7903 | 1308.1167 |  | 1200 | 870.0981 | 1547.171 | 1934.7061
| 1600 | 874.5525 | 1553.1102 | 1942.1301 |  | 1600 | 1293.2686 | 2299.9691 | 2874.5902
| 2100 | 1245.7547 | 2215.335 | 2769.1687 |  | 2100 | 1844.1328 | 3278.4582 | 4098.0728
| 2400 | 1523.414 | 2706.8068 | 3383.8797 |  | 2400 | 2253.94 | 4007.4994 | 5009.7455
| 2700 | 1826.315 | 3245.7924 | 4057.9829 |  | 2700 | 2702.3523 | 4804.8419 | 6006.0523
Cooling outputs at calculation conditions without correction
| F2C 110-230 |  |  |  |  | F2C 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 81.7865 | 145.3983 | 181.7478 |  | 850 | 121.0275 | 215.619 | 269.3172
| 1200 | 163.573 | 291.2096 | 363.9087 |  | 1200 | 242.055 | 430.4119 | 538.2214
| 1600 | 243.2942 | 432.0641 | 540.2867 |  | 1600 | 359.7781 | 639.8349 | 799.6904
| 2100 | 346.56 | 616.2903 | 770.3629 |  | 2100 | 513.0245 | 912.0436 | 1140.0545
| 2400 | 423.8029 | 753.0143 | 941.3711 |  | 2400 | 627.03 | 1114.8576 | 1393.6753
| 2700 | 508.0678 | 902.9562 | 1128.9018 |  | 2700 | 751.7751 | 1336.6726 | 1670.8407
Reynolds numbers at Twater=70 dC and (Tflow-Trtn) according to calculation values
| F4C 170-340 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 363.5238 | 646.2645 | 807.8306 |  | 850 | 537.9417 | 958.3808 | 1197.058
| 1200 | 727.0475 | 1294.3649 | 1617.4971 |  | 1200 | 1075.8834 | 1913.0897 | 2392.2801
| 1600 | 1081.3914 | 1920.4336 | 2401.46 |  | 1600 | 1599.1373 | 2843.9308 | 3554.4545
| 2100 | 1540.386 | 2739.28 | 3424.1 |  | 2100 | 2280.2854 | 4053.8407 | 5067.3009
| 2400 | 1883.714 | 3346.9889 | 4184.1952 |  | 2400 | 2787.0155 | 4955.3062 | 6194.5917
| 2700 | 2258.2536 | 4013.4492 | 5017.7294 |  | 2700 | 3341.481 | 5941.2267 | 7426.5333
Reynolds numbers at calculation conditions
| F4C 170-340 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 142.1143 | 252.6476 | 315.8095 |  | 850 | 210.3004 | 374.665 | 467.9723
| 1200 | 284.2286 | 506.013 | 632.3368 |  | 1200 | 420.6009 | 747.8944 | 935.2269
| 1600 | 422.7541 | 750.7654 | 938.8156 |  | 1600 | 625.1593 | 1111.7931 | 1389.562
| 2100 | 602.1914 | 1070.8815 | 1338.6018 |  | 2100 | 891.4442 | 1584.7897 | 1980.9871
| 2400 | 736.4104 | 1308.4564 | 1635.7499 |  | 2400 | 1089.5429 | 1937.2045 | 2421.685
| 2700 | 882.8312 | 1568.9992 | 1961.6079 |  | 2700 | 1306.3031 | 2322.6357 | 2903.2946
Re corrected heat outputs - W
| F4C 170-340 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 71.3525 | 128.5502 | 161.4112 |  | 850 | 106.581 | 192.1107 | 240.9021
| 1200 | 144.9683 | 260.8293 | 327.1207 |  | 1200 | 216.1145 | 387.8935 | 486.6204
| 1600 | 217.2405 | 389.4047 | 488.5139 |  | 1600 | 323.3498 | 579.8599 | 726.8267
| 2100 | 311.2863 | 558.2416 | 699.8411 |  | 2100 | 463.5262 | 830.2899 | 1040.5991
| 2400 | 381.8491 | 683.8823 | 857.3166 |  | 2400 | 568.1016 | 1017.3388 | 1274.9565
| 2700 | 458.9845 | 821.9171 | 1030.303 |  | 2700 | 682.7425 | 1222.2495 | 1531.4741
Flow resistance / Pressure drop - Pa
| F4C 170-340 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 53.7236 | 137.2141 | 197.1827 |  | 850 | 101.8009 | 260.2058 | 373.144
| 1200 | 375.8741 | 946.0652 | 1350.4755 |  | 1200 | 703.9923 | 1765.1801 | 2250.07
| 1600 | 1121.0127 | 2778.8371 | 3490.2627 |  | 1600 | 2081.0929 | 2851.0047 | 3136.5148
| 2100 | 2859.4628 | 4313.1265 | 4394.493 |  | 2100 | 5295.58 | 5099.9636 | 6193.7412
| 2400 | 4746.0128 | 5215.9841 | 6353.4372 |  | 2400 | 5121.1228 | 7363.771 | 10360.1636
| 2700 | 7581.6558 | 7386.9989 | 8991.8265 |  | 2700 | 6273.284 | 10700.7193 | 24132.5946
Re numbers according to selected fan speed
|  | F4C 170-340 |  |  |  | F4V 170-340
|  | Length |  |  |  | Length
|  | Lc, mm | Re |  |  | Lc, mm | Re
|  | 850 | 252.6476 |  |  | 850 | 374.665
|  | 1200 | 506.013 |  |  | 1200 | 747.8944
|  | 1600 | 750.7654 |  |  | 1600 | 1111.7931
|  | 2100 | 1070.8815 |  |  | 2100 | 1584.7897
|  | 2400 | 1308.4564 |  |  | 2400 | 1937.2045
|  | 2700 | 1568.9992 |  |  | 2700 | 2322.6357
Cooling outputs in Watts
Pressure drop in Pascal
|  | F4C 170-340 |  |  |  | F4V 170-340
|  | Length | OP and Δp |  |  | Length | OP and Δp
|  | Lc, mm | W | Pa |  | Lc, mm | W | Pa
|  | 850 | 128.5502 | 137.2141 |  | 850 | 192.1107 | 260.2058
|  | 1200 | 260.8293 | 946.0652 |  | 1200 | 387.8935 | 1765.1801
|  | 1600 | 389.4047 | 2778.8371 |  | 1600 | 579.8599 | 2851.0047
|  | 2100 | 558.2416 | 4313.1265 |  | 2100 | 830.2899 | 5099.9636
|  | 2400 | 683.8823 | 5215.9841 |  | 2400 | 1017.3388 | 7363.771
|  | 2700 | 821.9171 | 7386.9989 |  | 2700 | 1222.2495 | 10700.7193
Water flow rates, L/h
| F4C 110-230 |  |  |  |  | F4V 170-340
| Length |  | Fan speed |  |  | Length |  | Fan speed
| Lc, mm | 1 | 2 | 3 |  | Lc, mm | 1 | 2 | 3
| 850 | 10.2414 | 18.4511 | 23.1677 |  | 850 | 15.2978 | 27.574 | 34.5771
| 1200 | 20.8076 | 37.4373 | 46.9523 |  | 1200 | 31.0193 | 55.6751 | 69.8455
| 1600 | 31.1809 | 55.892 | 70.1173 |  | 1600 | 46.411 | 83.2284 | 104.3228
| 2100 | 44.6795 | 80.1255 | 100.4495 |  | 2100 | 66.5308 | 119.1731 | 149.3592
| 2400 | 54.8075 | 98.1589 | 123.0523 |  | 2400 | 81.5407 | 146.0206 | 182.9969
| 2700 | 65.8789 | 117.9713 | 147.8813 |  | 2700 | 97.9953 | 175.4318 | 219.8154

## F1P (hidden)
AQUILO F1P | [9 empty] | 021017 MII
Re corrected heat outputs
|  | Tflow = | 75 | oC |  |  |  | 1 | low
|  | Trtn = | 65 | oC |  | Fan speed = | 2 | 2 | middle*
|  | Troom = | 20 | oC | *) Recommended design value! |  |  | 3 | high
|  | ΔTln | 49.8329 | K
Output in Watts
F1P 90
| Total length | Width, mm
| L, mm | 180 | 260
| 1000 | 833.998 | 1254.997
| 1250 | 1108.9973 | 1668.996
| 1500 | 1379.9967 | 2074.995
| 1750 | 1644.9961 | 2472.9941
| 2000 | 1906.9954 | 2865.9931
| 2250 | 2165.9948 | 3254.9922
| 2500 | 2422.9942 | 3639.4913
| 2750 | 2676.9936 | 4020.9904
| 3000 | 2929.993 | 4398.9894
F1P 90-180 |  |  |  |  | 1.0529
F1P 90-260 |  |  |  |  | 1.0538
Fan f. | 1
L-Lc = | 0.32
Inner diam. = | 11
Number of parallel pipe loops = |  |  | 1 | 180
|  |  | 2 | 260
Re calculation:
[7 empty] | - Water flow rate |  | =D6/((D7-D8)/1,163
[7 empty] | - Velocity of water |  | =D11*4/(D10^2*3,142)/3,6
[7 empty] | - Density of water |  | =-0,003268*D12^2-0,12113*D12+1002,23
[7 empty] | - Viscosity of water |  | =-0,000001568*D12^3+0,0003846*D12^2-0,03584*D12+1,577
[7 empty] | - Reynold’s number |  | =D13*D10/1000/(D15*0,000001)
[7 empty] | - Correction factor |  | =0,0952*LN(D16)+0,1663
Reynold's numbers
F1T 90
| Total length | Width, mm
| L, mm | 180 | 260
| 1000 | 5554.6735 | 4179.3669
| 1250 | 7386.1957 | 5558.0036
| 1500 | 9191.0776 | 6909.9999
| 1750 | 10955.9989 | 8235.356
| 2000 | 12700.94 | 9544.0618
| 2250 | 14425.9009 | 10839.4475
| 2500 | 16137.5416 | 12119.848
| 2750 | 17829.2021 | 13390.2584
| 3000 | 19514.2025 | 14649.0136
[5 empty] | FAIL | = Negative ΔTln, too low water flow rate or faulty fan speed
F1P 90
| Total length | Width, mm
| L, mm | 260 | 290
| 1000 | 823.2828 | 1204.8843
| 1250 | 1124.8354 | 1647.648
| 1500 | 1428.4264 | 2091.4643
| 1750 | 1730.2338 | 2533.9323
| 2000 | 2032.6395 | 2976.8549
| 2250 | 2334.963 | 3420.3399
| 2500 | 2637.8741 | 3863.0561
| 2750 | 2939.8049 | 4306.1482
| 3000 | 3242.8315 | 4748.5798

## F2C (hidden)
AQUILO F2C | [9 empty] | 021017 MII
Re corrected heat outputs
|  | Tflow = | 75 | oC |  |  |  | 1 | low
|  | Trtn = | 65 | oC |  | Fan speed = | 2 | 2 | middle*
|  | Troom = | 20 | oC | *) Recommended design value! |  |  | 3 | high
|  | ΔTln | 49.8329 | K | Note. Negative ΔTln value = cooling mode
Output in Watts
F2C 110
| Total length | Width, mm
| L, mm | 240
| 600 | 864.9978
| 1000 | 1818.9954
| 1400 | 2731.9931
| 1800 | 3620.9908
F2C 110 |  |  |  |  | 1.1112
Fan | 1
L-Lc = | 0.28
Inner diam. = | 8.52
Number of parallel pipe loops = |  |  | 1
Re calculation:
[7 empty] | - Water flow rate |  | =D6/((D7-D8)/1,163
[7 empty] | - Velocity of water |  | =D11*4/(D10^2*3,142)/3,6
[7 empty] | - Density of water |  | =-0,003268*D12^2-0,12113*D12+1002,23
[7 empty] | - Viscosity of water |  | =-0,000001568*D12^3+0,0003846*D12^2-0,03584*D12+1,577
[7 empty] | - Reynold’s number |  | =D13*D10/1000/(D15*0,000001)
[7 empty] | - Correction factor |  | =0,0952*LN(D16)+0,1663
Reynold's numbers
F2C 110
| Total length | Width, mm
| L, mm | 240
| 600 | 7438.037
| 1000 | 15641.1916
| 1400 | 23491.7997
| 1800 | 31136.0391
[5 empty] | FAIL | = Too low water flow rate or faulty fan speed
F2C 110
| Total length | Width, mm
| L, mm | 240
| 600 | 877.9272
| 1000 | 1974.9007
| 1400 | 3071.9391
| 1800 | 4168.6684

## F4C (hidden)
AQUILO F4C | [9 empty] | 021017 MII
Re corrected heat outputs
|  | Tflow = | 75 | oC |  |  |  | 1 | low
|  | Trtn = | 65 | oC |  | Fan speed = | 2 | 2 | middle*
|  | Troom = | 20 | oC | *) Recommended design value! |  |  | 3 | high
|  | ΔTln | 49.8329 | K | Note. Negative ΔTln value = cooling mode
Output in Watts
F4C 140
| Total length | Width, mm
| L, mm | 240
| 1250 | 1651.9958
| 2000 | 3119.9921
| 2750 | 4528.9885
F4C 140 |  |  |  |  | 1.1129
| 30.87 | * | ΔT | ^
Fan f. | 1
L-Lc = | 0.52
Inner diam. = | 8.52
Number of parallel pipe loops = |  |  | 3
Re calculation:
[7 empty] | - Water flow rate |  | =D6/((D7-D8)/1,163
[7 empty] | - Velocity of water |  | =D11*4/(D10^2*3,142)/3,6
[7 empty] | - Density of water |  | =-0,003268*D12^2-0,12113*D12+1002,23
[7 empty] | - Viscosity of water |  | =-0,000001568*D12^3+0,0003846*D12^2-0,03584*D12+1,577
[7 empty] | - Reynold’s number |  | =D13*D10/1000/(D15*0,000001)
[7 empty] | - Correction factor |  | =0,0952*LN(D16)+0,1663
Reynold's numbers
F4C 140
| Total length | Width, mm
| L, mm | 240
| 1250 | 4735.1807
| 2000 | 8942.8085
| 2750 | 12981.3287
[5 empty] | FAIL | = Too low water flow rate or faulty fan speed
F4C 140
| Total length | Width, mm
| L, mm | 240
| 1250 | 1605.6676
| 2000 | 3221.3519
| 2750 | 4836.7997